| Manual of SC Series IO Module |  |
| --- | --- |

Content:

1 Overview	3

1.1 Reference Documents	4

1.1 Safety Instructions	4

1.2 Product Introduction	4

1.2.1 Product Selection List	5

2 Product Introduction	6

2.1 Module Appearance	7

2.1.1 Power Supply Module	7

2.1.2 IO Module	8

2.1.3 Placeholder Module	9

2.2 Module Signals	10

2.2.1 Power Module	10

2.2.1.1 SC9001 Power Module	10

2.2.2 Digital Input Module	11

2.2.3 Digital Output Module	13

2.2.4 Analog Input Module	15

2.2.4.1 SC3228 (8-channel ±10V Analog Input Module)	15

2.2.4.2 SC3238 (8-channel 0..20mA Analog Input Module)	18

2.2.4.3 SC 3248 (8-channel 4…0mA Analog Input Module)	20

2.2.4.4 SC3274 (4-channel Thermocouple Temperature Acquisition Module)	22

2.2.5 Analog Output Module	25

2.2.5.1 SC4224 (4-channel ±10V Analog Output Module)	25

2.2.5.2 SC4234 (4-channel 0…0mA Analog Output Module)	27

2.2.5.3 SC4244 (4-channel 4..20mA Analog Output Module)	29

2.2.6 Encoder Acquisition Module	31

2.2.6.1 SC5032 (2-channel Encoder Acquisition Module)	31

2.2.7 Special Module	33

2.2.7.1 SC9100 Placeholder Module	33

3 Mechanical Installation	34

3.1 Dimensions	35

3.2 Backplane Installation Method	36

3.3 Rail Installation Method	37

3.4 Mechanical Position Coding	37

4 Electrical Installation	39

4.1 Power Supply	40

4.2 Ether CAT Network Connection	41

4.3 Ether CAT Bus Topology	41

4.4 Input and Output Signals	42

5 EtherCAT Communication	43

5.1 About EtherCAT	44

5.1.1 EtherCAT Introduction	44

5.1.2 EtherCAT State Machine	44

5.1.3 CoE Interface	44

5.1.4 Distributed Clock	45

5.2 EtherCAT Parameters of Analog I/O Modules	46

5.2.1 4 | 8-channel, -10…10V (16bit) Analog Input Module	46

5.2.2 4 | 8-channel, 0…20mA (16bit) Analog Input Module	50

5.2.3 4 | 8-channel, 4…20mA (16bit) Analog Input Module	54

5.2.4 4-channel, -10…10V (16bit) Analog Output Module	58

5.2.5 4-channel, 0…20mA (16bit) Analog Output Module	63

5.2.6 4-channel, 4…20mA (16bit) Analog Output Module	68

5.2.7 Thermocouple Temperature Acquisition Module	73

5.3 Encoder Input Acquisition Module EtherCAT Parameters	75

5.3.1 PDO Process Data	75

5.3.2 SDO Service Data	76

6 Special Features	78

6.1 Data Calibration	79

7 FAQ	80

Overview

This chapter provides essential information about the product, including a summary of its key features and technical specifications.

Reference Documents

Please refer to the following list for the product documentation. It is important to read this information before using the product.

| Document Name | Document Objectives | Document Content | Document Archive |
| --- | --- | --- | --- |
| User Manual | Must read before using the product | Functional description of the product and related setup instructions | Download from Nodaga’s official website or get it from a local distributor |

  - Safety Instructions

To ensure safety during equipment operation, this manual incorporates the following icons to offer users extra safety information.

| Icon | Description |
| --- | --- |
|  | Warning: indicates a potential hazard that could lead to death, severe injury, or substantial property damage if not avoided. |
|  | Danger: indicates an immediate hazard that could result in death, severe injury, or major property damage if not avoided. |
|  | Note: This indicates essential information. |

Product Introduction

The SC series IO modules encompass a range of modules, including power supply, placeholder, digital input, digital output, analog input, and analog output. Each sub-series offers modules with various functionalities and specifications. These modules can be combined to create sophisticated automation solutions.

The SC series modules eliminate the need for additional couplers, offering the same signal types and quantities as existing products but with significantly reduced size. To custom signal distribution boards and prefabricated wiring harnesses enable ultra-compact installations and quick wiring, enhance electrical cabinet space utilization and wiring efficiency while preventing errors. Additionally, with extra prefabricated module frames, traditional DIN rail installation is possible, making them suitable for applications in logic control, bus data acquisition, distributed control, monitoring, industrial robotics, CNC machines, and more.

| Product Features | Advantages |
| --- | --- |
| Ultra-compact design | Enhanced electrical cabinet space utilization |
| Mechanical protection lock | Prevent module slippage and detachment |
| Mechanical coding | Avoid misinsertion |
| Custom signal distribution board and prefabricated wiring harness | Efficient wiring and installation process |
| Onboard relay capability | Save installation and wiring of extra components |
| Direct RJ45 communication connection | Save module and installation space |
| Available prefabricated module frames | Compatible with traditional DIN rail installation |

Product Selection List

| SINSEGYE Model | Specification Description |
| --- | --- |
| SC1116 | 16-channel digital input module, NPN type, 24VDC, filtering 3ms |
| SC1216 | 16-channel digital input module, PNP type, 24VDC, filtering 3ms |
| SC2116 | 16-channel digital output module, NPN type, 24VDC, filtering 0.5A |
| SC2216 | 16-channel digital output module, PNP type, 24VDC, filtering 0.5A |
| SC3228 | 8-channel analog voltage input module, single input, ±10V, 16 bit |
| SC3238 | 8-channel analog current input module, 0mA-20mA, 16 bit |
| SC3248 | 8-channel analog current input module, 4mA-20mA, 16 bit |
| SC3258 | 8-channel analog voltage input module, differential input, 0-10V, 16 bit |
| SC4224 | 4-channel analog voltage output module, -10V-+10V, 16 bit |
| SC4234 | 4-channel analog current output module, 0-20mA, 16 bit |
| SC4244 | 4-channel analog current output module, 4-20mA, 16 bit |
| SC3284 | 4-channel thermocouple input module, 16 bit |
| SC3274 | 4-channel thermal resistor input module, 16 bit |
| SC9001 | Power supply module |
| SC9100 | Placeholder module |
| SC3208 | 4-channel analog voltage input module, 4-channel current input module |
| SC5032 | 2-channel 5V differential input counter module |

Product Introduction

Module Appearance

Power Supply Module

②

③

④

⑤

①

- The power supply module includes SC9001.

- Bottom view of power supply module.

- Mechanical positioning posts (7&8) for the power supply module.

- Mechanical positioning holes (7&8) for the power supply module.

- Installation location of the power supply module on the signal distribution board.

IO Module

④

⑤

①

②

③

- I/O module.

- Bottom view of the I/O module.

- Mechanical positioning posts for the I/O module.

SC1XXX modules have a mechanical coding of 1&3.

SC2XXX modules have a mechanical coding of 1&4.

SC3XXX modules have a mechanical coding of 1&5.

SC4XXX modules have a mechanical coding of 1&7.

- Mechanical positioning holes for the I/O module.

- Installation location of the I/O module on the signal distribution board, requiring the alignment of positioning posts and holes.

Placeholder Module

①

②

③

- Placeholder module SC9100.

- Bottom view of the placeholder module (Note: The placeholder module does not have mechanical coding).

- Installation area for the placeholder module.

Module Signals

Power Module

SC9001 Power Module

For SC series I/O module, SC9001 supplies 3.3V power to other modules.

A

B

C

A: Us 3.3V power supply statusindicator

| Logo | Object | Color | Description |
| --- | --- | --- | --- |
| Us | Us 3.3V Power supply | White | On: Us 3.3V Power supply Off: Us 3.3V Resetting the power supply status |

B:Pin Definitions

| Pin | Name | Direction | Description |
| --- | --- | --- | --- |
| 1,2 | Us 3.3V | O | Us 3.3V output pin, used for communication power supply of post stage |
| 3,4,9,10,15,16 | Us GND | O | Us GND output pin, used for communication power supply of post stage |
| 5~8,11~14,19~32 | NC | - | Not connected |
| 17,18 | SW1,SW2 | - | Reset pin, for cooperative use |
| 33~35 | Us 0V | I | Us 0V input pin, used for power supply of the power module |
| 36~38 | Us 24V | I | Us 24V input pin, used for power supply of the power module |
| 39,40 | PE | - | Ground |

C: Reset Function Wiring Diagram

To utilize the reset function of SC9001, connect the reset pins SW1 and SW2 to the switch. Short time pres this button (to connect SW1 and SW2) to restart the power module.

Technical Parameters

| Technical Parameters | SC9001 |
| --- | --- |
| Short circuit protection | Yes |
| Input voltage | 24 VDC (-15 %/ +20 %) |
| Input current | ＜1mA +load |
| Rated output current | 3A |
| Short circuit protection current | 4A |
| Operating temperature | ﹣25 ℃～﹢60 ℃ |
| Storage temperature | ﹣40 ℃～﹢85 ℃ |
| Relative humidity | 95 %，No condensation |
| External dimensions | ～12 x 62 x 55 mm |
| Weight | ～28 g |
| Installation | PCB (signal distribution board supports various needs such as rail and screw) |
| Installation position | 35mm gap between upper and lower installation |
| Position coding | 7&8 |
| Protection class | IP20 |

Digital Input Module

SC1116 and SC1216 are 16-channel digital input modules for NPN and PNP, respectively. By default, they provide 3ms input filter, which can effectively filter out input signal jitter and spikes, thereby avoiding interference from erroneous states.

A

B

A:Status indicator

| Logo | Object | Color | Description |
| --- | --- | --- | --- |
| RUN | Slave State Machine | White | Off: Initialization state Flash: PrepOP state Single flash: SafeOP state Remain On: OP state Flicker: Boot mode |
| L/Ax | Communication | White | Off: No valid communication network established, or network port damaged Remain On/Occasional Flash: Communication established, waiting for data Flash: Normal data communication |
| 1~16 | DI Input Channels 1~16 | White | Off: No valid input signal On: Input signal is valid |

B:Pin Definition

| Pin | Name | Direction | Description |
| --- | --- | --- | --- |
| 1,2 | Us 3.3V | O | Us 3.3V output pin, used for communication power supply of post stage |
| 3,4,9,10,15,16 | Us GND | O | Us GND output pin, used for communication power supply of post stage |
| 5 | Rx0+ | I | Preceding stage module Ethernet receive + |
| 6 | Tx1+ | O | Post stage module Ethernet transmit + |
| 7 | Rx0- | I | Preceding stage module Ethernet receive - |
| 8 | Tx1- | O | Post stage module Ethernet transmit- |
| 11 | Tx0+ | O | Preceding stage module Ethernet transmit + |
| 12 | Rx1+ | I | Post stage module Ethernet receive + |
| 13 | Tx0- | O | Preceding stage module Ethernet transmit- |
| 14 | Rx1- | I | Post stage module Ethernet receive- |
| 17~32 | DI 1~16 | I | Digital input channels 1~16 |
| 33~35 | Up 0V | I | Field side power 0V |
| 36~38 | Up 24V | I | Field side power 24V |
| 39,40 | PE | - | Ground |

Technical Parameters

| Technical Parameters | SC1116 | SC1216 |
| --- | --- | --- |
| Number of input channels | 16 |  |
| Input voltage | 24 V DC (-15 %/ +20 %) |  |
| Input “0” voltage range | 18V～30V | -3V～+5V (EN61131-2, type 1/3) |
| Input “1” voltage range | 0V～7V | 11V～30V (EN 61131-2, type 3) |
| Input current | Typical Value 3mA |  |
| Input filtering | 3ms |  |
| Us power consumption | Typical Value 145mA | Typical Value 155mA |
| Electrical isolation withstand voltage | 500 V (Communication and Field Voltage) |  |
| Operating temperature | ﹣25 ℃～﹢85 ℃ |  |
| Storage temperature | ﹣40 ℃～﹢85 ℃ |  |
| Relative humidity | 95 %，No condensation |  |
| Dimensions | ～12 x 62 x 55 mm |  |
| Weight | ～23 g |  |
| Installation position | 35mm gap between upper and lower installation |  |
| Position coding | 1 & 3 |  |
| Protection class | IP20 |  |

Digital Output Module

SC2116 and SC2216 are 16-channel NPN and PNP digital output modules, respectively. The maximum output current per channel is 500mA. Their outputs have overload and short-circuit protection functions, which can effectively prevent short-circuit problems caused by miswiring.

B

A

A:Status indicator

| Logo | Object | Color | Description |
| --- | --- | --- | --- |
| RUN | Slave state machine | White | Off: Initial state Flash: Preparation for OP state Single Flash: Safe OP state Remain on: OP state Flicker: Boot mode |
| L/Ax | Communication | White | Off: No valid communication network available, or network port damaged Remain On/Occasional flash: Communication established, waiting for data Flash: Normal data transmission |
| 1~16 | DO Output Channel 1~16 | White | Off: No valid signal output On: Valid signal output |

B:Pin Definition

| Pin | Name | Direction | Description |
| --- | --- | --- | --- |
| 1,2 | Us 3.3V | O | US 3.3V Output Pin: Used for communication powering of post stage I/O equipment |
| 3,4,9,10,15,16 | Us GND | O | US GND Output Pin: Used for communication powering of post stage I/O equipment |
| 5 | Rx0+ | I | Preceding stage module Ethernet receive + |
| 6 | Tx1+ | O | Post stage module Ethernet transmit + |
| 7 | Rx0- | I | Preceding stage module Ethernet receive - |
| 8 | Tx1- | O | Post stage module Ethernet transmit- |
| 11 | Tx0+ | O | Preceding stage module Ethernet transmit + |
| 12 | Rx1+ | I | Post stage module Ethernet receive + |
| 13 | Tx0- | O | Preceding stage module Ethernet transmit- |
| 14 | Rx1- | I | Post stage module Ethernet receive- |
| 17~32 | DO 1~16 | O | Digital input channels 1~16 |
| 33~35 | Up 0V | I | Field side power 0V |
| 36~38 | Up 24V | I | Field side power 24V |
| 39,40 | PE | - | Ground |

Technical Parameters

| Technical Parameters | SC2116 | SC2216 |
| --- | --- | --- |
| Number of output channels | 16 |  |
| Supply voltage | 24 V DC (-15 %/ +20 %) |  |
| Type of load | Resistor, Inductor, Lamp type |  |
| Output current | Output current |  |
| Reverse voltage protection | Have |  |
| Switching duration | Ton: Typical value 15us; Toff: Typical value 300us |  |
| Us power consumption | Typical value 145mA | Typical value 155mA |
| Current consumption by the load | ＜1mA +Load | Typical value 9mA +Load |
| Electrical isolation withstand voltage | 500 V (Communication and field voltage) |  |
| Operating temperature | ﹣25 ℃～﹢85 ℃ |  |
| Storage temperature | ﹣40 ℃～﹢85 ℃ |  |
| Relative humidity | 95 %, No condensation |  |
| Dimensions | ～12 x 62 x 55 mm |  |
| Weight | ～24 g |  |
| Install | PCB (The signal distribution board supports various requirements, including rail and screw) |  |
| Installation position | 35mm gap between upper and lower installation |  |
| Position coding | 1 & 4 |  |

Analog Input Module

SC3228 (8-channel ±10V Analog Input Module)

SC3228 is an 8-channel module designed for -10V to +10V analog input signal acquisition, featuring a 16-bit resolution and single-ended input configuration.

A

B

A:SC3228 Status indicator

| Logo | Object | Color | Description |
| --- | --- | --- | --- |
| RUN | Slave station state machine | White | Off: Initialization state Flash: PrepOP state Single Flash:SafeOP state Remain on: OP state Flicker: Boot mode |
| L/Ax | Communication | White | Off: No valid communication connection, or the port is damaged Remain On/Occasionally flash: communication Connected, waiting for data Flash: Data is sent and received normally |
| E1~E8 | AI Input channel 1~8 | White | Off: No errors On: Error, including over-range or power supply abnormality. |

B:SC3228 Pin Definitions

| Pin | Name | Direction | Description |
| --- | --- | --- | --- |
| 1,2 | Us 3.3V | O | US 3.3V output pin, used for communication power supply of post stage I/O |
| 3,4,9,10,15,16 | Us GND | O | US GND output pin, used for communication power supply of post stage I/O |
| 5 | Rx0+ | I | Preceding stage module Ethernet receive + |
| 6 | Tx1+ | O | Post stage module Ethernet transmit + |
| 7 | Rx0- | I | Preceding stage module Ethernet receive - |
| 8 | Tx1- | O | Post stage module Ethernet transmit- |
| 11 | Tx0+ | O | Preceding stage module Ethernet transmit + |
| 12 | Rx1+ | I | Post stage module Ethernet receive + |
| 13 | Tx0- | O | Preceding stage module Ethernet transmit- |
| 14 | Rx1- | I | Post stage module Ethernet receive- |
| 18,20,22,24 26,28,30,32 | AI 1~8 | I | Digital input channels 1~8 |
| 17,19,21,23 25,27,29,31 | AGND | I | Analog ground |
| 33~35 | Up 0V | I | 0V power supply at the field side |
| 36~38 | Up 24V | I | 24V power supply at the field side |
| 39,40 | PE | - | Ground |

Technical Parameters

| Technical Parameters | SC3228 |
| --- | --- |
| Number of input channels | 8(Single-ended two-wire configuration) |
| Supply voltage | 24 V DC (-15 %/ +20 %) |
| Signal voltage | -10V～﹢10V |
| Resolution | 16-bit |
| Input impedance | ～10MΩ |
| Input filter cutoff frequency | 10KHz |
| Conversion time | ～400μs |
| Measurement error | ＜0.1%(0～55℃，relative to full scale) |
| Distributed Clock (64bit) | Supports synchronized switching between SM and DC |
| Distributed clock accuracy | << 1μs |
| US power consumption | Typical value 165mA |
| Process mirror bit width | 16-bit |
| Galvanically isolated withstand voltage | 500 V (Communication with field voltage) |
| Operating temperature | ﹣25 ℃～﹢85 ℃ |
| Storage temperature | ﹣40 ℃～﹢85 ℃ |
| Relative humidity | 95 %，No condensation |
| Dimension | ～12 x 62 x 55 mm |
| Weight | ～25 g |
| Installation | PCB (The signal distribution board supports various requirements, including rail and screw) |
| Installation location | 35mm gap between upper and lower installation |
| Location code | 1 & 5 |
| Protection class | IP20 |

SC3238 (8-channel 0..20mA Analog Input Module)

SC3238 is an 8-channel, 0 to 20mA analog input acquisition module with 16-bit resolution and single-ended input.

A

B

A:SC3238Status indicator

| Logo | Object | Color | Description |
| --- | --- | --- | --- |
| RUN | Slave station state machine | White | Off: Initialization state Flash: PrepOP status Single Flash: SafeOP status Remain On: OP status Flicker: Boot mode |
| L/Ax | Communication | White | Off: No valid communication network established, or network port damaged Remain On/Occasional flash: communication established, waiting for data Flash: Normal data communication |
| E1~E8 | AI Input channel 1~8 | White | Off: No error On: Error status, including over-range, Abnormal Up power supply, etc. |

B:SC3238 Pin Definitions

| Pin | Name | Direction | Description |
| --- | --- | --- | --- |
| 1,2 | Us 3.3V | O | Us 3.3V output pin for communication power supply to post stage I/O devices |
| 3,4,9,10,15,16 | Us GND | O | Us GND output pin for communication power supply of post stage I/O devices |
| 5 | Rx0+ | I | Preceding stage module Ethernet receive + |
| 6 | Tx1+ | O | Post stage module Ethernet transmit + |
| 7 | Rx0- | I | Preceding stage module Ethernet receive - |
| 8 | Tx1- | O | Post stage module Ethernet transmit- |
| 11 | Tx0+ | O | Preceding stage module Ethernet transmit + |
| 12 | Rx1+ | I | Post stage module Ethernet receive + |
| 13 | Tx0- | O | Preceding stage module Ethernet transmit- |
| 14 | Rx1- | I | Post stage module Ethernet receive- |
| 18,20,22,24 26,28,30,32 | AI 1~8 | I | Digital input channels 1~8 |
| 17,19,21,23 25,27,29,31 | AGND | I | Analog ground |
| 33~35 | Up 0V | I | 0V power supply at the field side |
| 36~38 | Up 24V | I | 24V power supply at the field side |
| 39,40 | PE | - | Ground |

Technical Parameters

| Technical Parameters | SC3238 |
| --- | --- |
| Number of input channels | 8(Single-ended two-wire configuration) |
| Supply voltage | 24 V DC (-15 %/ +20 %) |
| Signal current | 0mA ～20mA |
| Resolution | 16-bit |
| Input impedance | ～200Ω |
| Input filter cutoff frequency | 10KHz |
| Conversion time | ～400μs |
| Measurement error | ＜0.1% (0～55℃，relative to full scale) |
| Distributed clock (64bit) | Support synchronous switching between SM and DC |
| Distributed clock accuracy | << 1μs |
| Us power supply consumption | Typical value 165mA |
| Process mirror bit width | 16-bit |
| Galvanic isolation withstand voltage | 500 V (Communication with field voltage) |
| Operating temperature | ﹣25 ℃～﹢85 ℃ |
| Storage temperature | ﹣40 ℃～﹢85 ℃ |
| Relative humidity | 95 %，No condensation |
| Dimension | ～12 x 62 x 55 mm |
| Weight | ～25 g |
| Installation | PCB (The signal distribution board supports various requirements, including rail and screw) |
| Mounting position | 35mm gap between upper and lower installation |
| Location code | 1 & 5 |
| Protection class | IP20 |

SC 3248 (8-channel 4…0mA Analog Input Module)

SC3248 is an 8-channel 4..20mA analog input acquisition module with 16-bit resolution and single-ended inputs.

A

B

C:SC3248 Status Indicator

| Logo | Object | Color | Description |
| --- | --- | --- | --- |
| RUN | Slave station state machine | White | Off: Initialization state Flash: PrepOP state Single Flash: SafeOP state Remain on: OP state Flicker: Boot mode |
| L/Ax | Communication | White | Off: No valid communication network established, or network port damaged Remain on/Occasional flash: communication established, waiting for data Flash: Normal data communication |
| E1~E8 | AI Input channel 1~8 | White | Off: No error On: Error status, including over-range, Up power supply abnormality, etc. |

D:SC3248 Pin Definitions

| Pin | Name | Direction | Description |
| --- | --- | --- | --- |
| 1,2 | Us 3.3V | O | Us 3.3V output pin for communication power supply to post stage I/O devices |
| 3,4,9,10,15,16 | Us GND | O | Us GND output pin for communication power supply of the post stage I/O device |
| 5 | Rx0+ | I | Preceding stage module Ethernet receive + |
| 6 | Tx1+ | O | Post stage module Ethernet transmit + |
| 7 | Rx0- | I | Preceding stage module Ethernet receive - |
| 8 | Tx1- | O | Post stage module Ethernet transmit- |
| 11 | Tx0+ | O | Preceding stage module Ethernet transmit + |
| 12 | Rx1+ | I | Post stage module Ethernet receive + |
| 13 | Tx0- | O | Preceding stage module Ethernet transmit- |
| 14 | Rx1- | I | Post stage module Ethernet receive- |
| 18,20,22,24 26,28,30,32 | AI 1~8 | I | Digital input channels 1~8 |
| 17,19,21,23 25,27,29,31 | AGND | I | Analog ground |
| 33~35 | Up 0V | I | 0V power supply at the field side |
| 36~38 | Up 24V | I | 24V power supply at the field side |
| 39,40 | PE | - | Ground |

Technical Parameters

| Technical Parameters | SC3248 |
| --- | --- |
| Number of input channels | 8(Single-ended two-wire configuration) |
| Supply voltage | 24 V DC (-15 %/ +20 %) |
| Signal current | 4mA ～20mA |
| Resolution | 16位 |
| Input impedance | ～200Ω |
| Input filter cutoff frequency | 10KHz |
| Conversion time | ～400μs |
| Measurement error | ＜0.1% (0～55℃，relative to full scale) |
| Distributed clock (64bit) | Support synchronous switching between SM and DC |
| Distributed clock accuracy | << 1μs |
| Us power supply consumption | Typical value 165mA |
| Process mirror bit width | 16 bit |
| Galvanic isolation withstand voltage | 500 V (Communication with field voltage) |
| Operating temperature | ﹣25 ℃～﹢85 ℃ |
| Storage temperature | ﹣40 ℃～﹢85 ℃ |
| Relative humidity | 95 %，No condensation |
| Dimension | ～12 x 62 x 55 mm |
| Weight | ～25 g |
| Installation | PCB (The signal distribution board supports various requirements, including rail and screw) |
| Mounting position | 35mm gap between upper and lower installation |
| Location code | 1 & 5 |
| Protection class | IP20 |

SC3274 (4-channel Thermocouple Temperature Acquisition Module)

SC3274 module is an EtherCAT bus-based analog input module with 4 inputs and 16-bit resolution for RTD temperature acquisition. It can simultaneously access 4 3-wire sensors and supports PT100, PT1000 and NI100 sensors.

Communication

indicator

通信指示灯

Front  view

Bottom view

Signal indicator

Communication indicator

| Logo | Object | Color | Description |
| --- | --- | --- | --- |
| RUN | Slave station state machine | White | Off: Initialization state Flash: PrepOP status Single flash: SafeOP status Remain on: OP status Flicker: Boot mode |
| L/Ax | Communication | White | Off: No valid communication network established, or network port damaged Remain on/Occasional flash: communication established, waiting for data Flash: Normal data communication |
| E1~E4 | RTD input channels 1~4 | Red | Off: No error On: Error status, including over-range, Up power supply abnormality, etc. |

Pin Definitions

| Pin | Name | Direction | Description |
| --- | --- | --- | --- |
| 1,2 | Us 3.3V | O | Us 3.3V output pin for communication power supply to post stage I/O devices |
| 3,4,9,10 | Us GND | O | Us GND output pin for communication power supply of the post stage I/O devices |
| 5 | Rx0+ | I | Preceding stage module Ethernet receive + |
| 6 | Tx1+ | O | Post stage module Ethernet transmit + |
| 7 | Rx0- | I | Preceding stage module Ethernet receive - |
| 8 | Tx1- | O | Post stage module Ethernet transmit- |
| 11 | Tx0+ | O | Preceding stage module Ethernet transmit + |
| 12 | Rx1+ | I | Post stage module Ethernet receive + |
| 13 | Tx0- | O | Preceding stage module Ethernet transmit- |
| 14 | Rx1- | I | Post stage module Ethernet receive- |
| 15 | SWDIO |  | MCU data line |
| 16 | SWCLK |  | MCU Clock Line |
| 17,18,23,24 | RTD 1~4+ | I | RTD 1~4+ Input |
| 19,20,25,26 | RTD 1~4- | I | RTD 1~4- input |
| 21,22,27,28 | RTDL 1~4- | I | RTDL 1~4- input |
| 29~32 | NC |  | Not connected |
| 33~35 | PGND | I | Field side power supply 0V |
| 36~38 | Up 24V | I | Field side power supply 24V |
| 39,40 | PE |  | Ground |

Technical Parameters

| Technical Parameters | SC3274 |
| --- | --- |
| Number of input channels | 4(Three-wire system) |
| Input filter cutoff frequency | Typical value 1 kHz |
| Transducer type | PT100, PT1000,NI100 |
| Conversion time | About 2ms~800ms |
| Measuring current | Typical value 5mA(Depends on the load) |
| Measuring range | -200℃…850℃ (Platinum sensor) -60℃…250℃(Nickel sensor) |
| Temperature range | Depends on range: +850°C (platinum sensor). -60°C...+250°C (nickel sensor) |
| Resolution | 0.1Celsius per person |
| Measurement error | < ±0.5°C for platinum sensors < ±1.5°C (range with extended temperature)) |
| Distributed clock (64bit) | - |
| Us power supply consumption | Typical value 165mA |
| Galvanic isolation withstand voltage | 500 V (Communication with field voltage) |
| Operating temperature | ﹣25 ℃～﹢85 ℃ |
| Storage temperature | ﹣40 ℃～﹢85 ℃ |
| Relative humidity | 95 %, No condensation |
| Overall dimension | ～12 x 62 x 55 mm |
| Weight | ～25 g |
| Installation | PCB (The signal distribution board supports various requirements, including rail and screw) |
| Mounting position | 35mm gap between upper and lower installation |
| Location code | 1 & 5 |
| Protection class | IP20 |

Wiring Schematic

Three wire system RTD 4

Three wire system RTD 3

Three wire system RTD 2

Three wire system RTD 1

SC3274

Analog Output Module

SC4224 (4-channel ±10V Analog Output Module)

SC4224 is a 4-channel ±10V analog voltage output module with 16-bit resolution. All output channels have a common ground potential and the output stage is powered by 24V supply.

A

B

A:SC4224 Status indicator

| Logo | Object | Color | Description |
| --- | --- | --- | --- |
| RUN | Slave station state machine | White | Off: Initialization state Flash: PrepOP status Single flash: SafeOP status Remain on: OP status Flicker: Boot mode |
| L/Ax | Communication | White | Off: No valid communication network established, or network port damaged Remain on/Occasional flash: communication established, waiting for data Flash: Normal data communication |
| E1~E4 | AO output channels 1~4 | White | Off: No error On: error status, including short circuit, Up power supply abnormality, etc. |

B:SC4224 Pin Definitions

| Pin | Name | Direction | Description |
| --- | --- | --- | --- |
| 1,2 | Us 3.3V | O | Us 3.3V output pin for communication power supply to post stage I/O devices |
| 3,4,9,10,15,16 | Us GND | O | Us GND output pin for communication power supply of the post stage I/O devices |
| 5 | Rx0+ | I | Preceding stage module Ethernet receive + |
| 6 | Tx1+ | O | Post stage module Ethernet transmit + |
| 7 | Rx0- | I | Preceding stage module Ethernet receive - |
| 8 | Tx1- | O | Post stage module Ethernet transmit- |
| 11 | Tx0+ | O | Preceding stage module Ethernet transmit + |
| 12 | Rx1+ | I | Post stage module Ethernet receive + |
| 13 | Tx0- | O | Preceding stage module Ethernet transmit- |
| 14 | Rx1- | I | Post stage module Ethernet receive- |
| 18,20,26,28 | AO 1~4 | I | Analog output 1~4 channels |
| 17,19,25,27 | AGND | I | Analog ground |
| 21~24,29~32 | NC | - | Not connected |
| 33~35 | Up 0V | I | Field side power supply 0V |
| 36~38 | Up 24V | I | Field side power supply 24V |
| 39,40 | PE | - | Ground |

Technical Parameters

| Technical Parameters | SC4224 |
| --- | --- |
| Number of output channels | 4(Single-ended two-wire configuration) |
| Supply voltage | 24 V DC (-15 %/ +20 %) |
| Signal voltage | -10V ～+10V |
| Load | ＞2KΩ (Short circuit protection) |
| Measurement error | ＜0.1% (0～55 ℃，relative to full scale) |
| Resolution | 16 bit |
| Conversion time | ～200μs |
| Distributed clock (64bit) | Support synchronous switching between SM and DC |
| Distributed clock accuracy | << 1μs |
| Us power supply consumption | Typical value 165mA |
| Up supply consumption | Typical value 26mA + load (＜5mA/channel) |
| Galvanic isolation withstand voltage | 500 V (Communication with field voltage) |
| Operating temperature | ﹣25 ℃～﹢85 ℃ |
| Storage temperature | ﹣40 ℃～﹢85 ℃ |
| Relative humidity | 95 %，No condensation |
| Dimension | ～12 x 62 x 55 mm |
| Weight | ～24 g |
| Installation | PCB (The signal distribution board supports various requirements, including rail and screw) |
| Mounting position | 35mm gap between upper and lower installation |
| Location code | 1 & 7 |
| Protection class | IP20 |

SC4234 (4-channel 0…0mA Analog Output Module)

SC4234 is a 4-channel 0..20mA analog current output module with 16-bit resolution, all output channels have a common ground potential and the output stage is powered by  24V supply.

A

B

A:SC4234Status indicator

| Logo | Object | Color | Description |
| --- | --- | --- | --- |
| RUN | Slave station state machine | White | Off: Initialization state Flash: PrepOP status Single Flash: SafeOP status Remain on: OP status Flicker: Boot mode |
| L/Ax | Communication | White | Off: No valid communication network established, or network port damaged Remain on/Occasional flash: communication established, waiting for data Flash: Normal data communication |
| E1~E4 | AO output channels 1~4 | White | Off: No error On: error status, including short circuit, Up power supply abnormality, etc. |

B:SC4234 Pin Definitions

| Pin | Name | Direction | Description |
| --- | --- | --- | --- |
| 1,2 | Us 3.3V | O | Us 3.3V output pin for communication power supply to post stage I/O devices |
| 3,4,9,10,15,16 | Us GND | O | Us GND output pin for communication power supply of the post stage I/O devices |
| 5 | Rx0+ | I | Preceding stage module Ethernet receive + |
| 6 | Tx1+ | O | Post stage module Ethernet transmit + |
| 7 | Rx0- | I | Preceding stage module Ethernet receive - |
| 8 | Tx1- | O | Post stage module Ethernet transmit- |
| 11 | Tx0+ | O | Preceding stage module Ethernet transmit + |
| 12 | Rx1+ | I | Post stage module Ethernet receive + |
| 13 | Tx0- | O | Preceding stage module Ethernet transmit- |
| 14 | Rx1- | I | Post stage module Ethernet receive- |
| 18,20,26,28 | AO 1~4 | I | Analog output 1~4 channels |
| 17,19,25,27 | AGND | I | Analog ground |
| 21~24,29~32 | NC | - | Not connected |
| 33~35 | Up 0V | I | Field side power supply 0V |
| 36~38 | Up 24V | I | Field side power supply 24V |
| 39,40 | PE | - | Ground |

Technical Parameters

| Technical Parameters | SC4234 |
| --- | --- |
| Number of output channels | 4(Single-ended two-wire configuration) |
| Supply voltage | 24 V DC (-15 %/ +20 %) |
| Signal current | 0mA～20mA |
| Load | ＜500Ω(Overload protection) |
| Measurement error | ＜0.1%(0～55℃, relative to full scale) |
| Resolution | 16 bit |
| Conversion time | ～200μs |
| Distributed clock (64bit) | Support synchronous switching between SM and DC |
| Distributed clock accuracy | << 1μs |
| Us power supply consumption | Typical value 165mA |
| Up supply consumption | Typical value 17mA + load (＜13.5mA/channel) |
| Galvanic isolation withstand voltage | 500 V(Communication with field voltage) |
| Operating temperature | ﹣25 ℃～﹢85 ℃ |
| Storage temperature | ﹣40 ℃～﹢85 ℃ |
| Relative humidity | 95 %, No condensation |
| Dimension | ～12 x 62 x 55 mm |
| Weight | ～24 g |
| Installation | PCB (The signal distribution board supports various requirements, including rail and screw) |
| Mounting position | 35mm gap between upper and lower installation |
| Location code | 1 & 7 |
| Protection class | IP20 |

SC4244 (4-channel 4..20mA Analog Output Module)

SC4244 is a 4-channel 4..20mA analog current output module with 16-bit resolution, all output channels have a common ground potential and the output stage is powered by 24V supply.

A

B

A:SC4244 Status Indicator

| Logo | Object | Color | Description |
| --- | --- | --- | --- |
| RUN | Slave station state machine | White | Off: Initialization state Flash: PrepOP status Single Flash: SafeOP status Remain on: OP status Flicker: Boot mode |
| L/Ax | Communication | White | Off: No valid communication network established, or network port damaged Remain on/Occasional flash: communication established, waiting for data Flash: Normal data communication |
| E1~E4 | AO output channels 1~4 | White | Off: No error On: error status, including short circuit, Up power supply abnormality, etc. |

B:SC4244 Pin Definitions

| Pin | Name | Direction | Description |
| --- | --- | --- | --- |
| 1,2 | Us 3.3V | O | Us 3.3V output pin for communication power supply to post stage I/O devices |
| 3,4,9,10,15,16 | Us GND | O | Us GND output pin for communication power supply of the post stage I/O device |
| 5 | Rx0+ | I | Preceding stage module Ethernet receive + |
| 6 | Tx1+ | O | Post stage module Ethernet transmit + |
| 7 | Rx0- | I | Preceding stage module Ethernet receive - |
| 8 | Tx1- | O | Post stage module Ethernet transmit- |
| 11 | Tx0+ | O | Preceding stage module Ethernet transmit + |
| 12 | Rx1+ | I | Post stage module Ethernet receive + |
| 13 | Tx0- | O | Preceding stage module Ethernet transmit- |
| 14 | Rx1- | I | Post stage module Ethernet receive- |
| 18,20,26,28 | AO 1~4 | I | Analog output 1~4 channels |
| 17,19,25,27 | AGND | I | Analog ground |
| 21~24,29~32 | NC | - | Not connected |
| 33~35 | Up 0V | I | Field side power supply 0V |
| 36~38 | Up 24V | I | Field side power supply 24V |
| 39,40 | PE | - | Ground |

Technical Parameters

| Technical Parameters | SC4244 |
| --- | --- |
| Number of output channels | 4(Single-ended two-wire configuration) |
| Supply voltage | 24 V DC (-15 %/ +20 %) |
| Signal current | 4mA～20mA |
| Load | ＜500Ω(Overload protection) |
| Measurement error | ＜0.1%(0～55℃，relative to full scale) |
| Resolution | 16 bit |
| Conversion time | ～200μs |
| Distributed clock (64bit) | Support synchronous switching between SM and DC |
| Distributed clock accuracy | << 1μs |
| Us power supply consumption | Typical value 165mA |
| Up supply consumption | Typical value 29mA + load(＜11mA/channel) |
| Galvanic isolation withstand voltage | 500 V(Communication with field voltage) |
| Operating temperature | ﹣25 ℃～﹢85 ℃ |
| Storage temperature | ﹣40 ℃～﹢85 ℃ |
| Relative humidity | 95 %，No condensation |
| Dimension | ～12 x 62 x 55 mm |
| Weight | ～24 g |
| Installation | PCB (The signal distribution board supports various requirements, including rail and screw) |
| Mounting position | 35mm gap between upper and lower installation |
| Location code | 1 & 7 |
| Protection class | IP20 |

Encoder Acquisition Module

SC5032 (2-channel Encoder Acquisition Module)

SC5032 module is an EtherCAT bus-based encoder acquisition module with two 5V differential encoder signal inputs, two encoder latching interfaces, two encoder signal access ports, pulse input indicator and latching signal indicator.

Channel and 5V indicator

Communication indicator

Front view

Bottom view

Status indicator

| Logo | Object | Color | Description |
| --- | --- | --- | --- |
| RUN | Slave station state machine | White | Off: Initialization state Flash: PrepOP status Single Flash: SafeOP status Remain on: OP status Flicker: Boot mode |
| L/Ax | Communication | White | Off: No valid communication network established, or network port damaged Remain on/Occasional flash: communication established, waiting for data Flash: Normal data communication |
| A1,B1,C1 Ａ2,B2,C2 | Phase A B C of encoder input | White | Off: no pulse input On: pulse input |
| L1,L2 | Encoder latching signal | White | Off: No latch signal input On: Latching signal input |
| 5V | 5V power indicator | White | Off: without 5V output On: 5V output |

Pin Definitions

| Pin | Name | Direction | Description |
| --- | --- | --- | --- |
| 1,2 | Us 3.3V | O | Us 3.3V output pin for communication power supply to post stage I/O devices |
| 3,4,9,10 | Us GND | O | Us GND output pin for communication power supply of the post stage I/O device |
| 5 | Rx0+ | I | Preceding stage module Ethernet receive + |
| 6 | Tx1+ | O | Post stage module Ethernet transmit + |
| 7 | Rx0- | I | Preceding stage module Ethernet receive - |
| 8 | Tx1- | O | Post stage module Ethernet transmit- |
| 11 | Tx0+ | O | Preceding stage module Ethernet transmit + |
| 12 | Rx1+ | I | Post stage module Ethernet receive + |
| 13 | Tx0- | O | Preceding stage module Ethernet transmit- |
| 14 | Rx1- | I | Post stage module Ethernet receive- |
| 15 | SWDIO |  | MCU data line |
| 16 | SWCLK |  | MCU clock line |
| 17,18,21 | ENC0_A_P,ENC0_B_P ENC0_Z_P | I | Encoder 0 phase A, B, Z input + |
| 19,20,23 | ENC0_A_N,ENC0_B_N ENC0_Z_N | I | Encoder 0 phase A, B, Z input - |
| 25,26,29 | ENC1_A_P, ENC1_B_P ENC1_Z_P | I | Encoder 1 phase A, B, Z input + |
| 27,28,31 | ENC1_A_N, ENC1_B_N ENC1_Z_N | I | Encoder 1 phase A, B, Z input - |
| 22 | VDD_5V | O | 5V output |
| 24 | NC |  | Not connected |
| 30,32 | LATCH_IN0 LATCH_IN1 | I | Latching input for encoder 0, 1 |
| 33~35 | Up 0V | I | Field side power supply 0V |
| 36~38 | Up 24V | I | Field side power supply 24V |
| 39,40 | PE | - | Ground |

Technology specification

| Technical Parameters | SC5032-0000 |
| --- | --- |
| Supply voltage | 24 V DC (-15 %/ +20 %) |
| Encoder input type | Incremental Encoders(A/B) |
| Number of input channels | 2 paths (EA+EB+EZ) |
| Input type | Differential |
| Signal voltage | 0～5 VDC |
| Pulse counting multiplier | 4x/2x (default 4x) |
| Pulse counting range | -2147483648 ～ +2147483648 |
| Counting Direction Reverse | Support |
| Us power consumption | Typical value 165mA |
| Isolation voltage | 500 V(Communication with field voltage) |
| Operating temperature | ﹣25 ℃～﹢85 ℃ |
| Storage temperature | ﹣40 ℃～﹢85 ℃ |
| Relative humidity | 95 %，No condensation |
| Dimension | ～12 x 62 x 55 mm |
| Weight | ～25 g |
| Installation | PCB (The signal distribution board supports various requirements, including rail and screw) |
| Mounting position | 35mm gap between upper and lower installation |
| Location code | 2 & 7 |
| Protection class | IP20 |

Special Module

SC9100 Placeholder Module

The placeholder module SC9100 is used to occupy a temporarily unused SC module slot on the signal distribution board and to provide a 3.3 V power supply and EtherCAT communication bridge for post stage modules. The power consumption of the Occupancy Module is negligible and does not need to be taken into account when selecting the power supply. The placeholder module SC9100 is not a slave.

A

A:SC9100 Status indicator

| Logo | Object | Color | Description |
| --- | --- | --- | --- |
| Us | Us 3.3V Power supply | White | On: Us 3.3V power supply is normal Off: Us 3.3V power supply is abnormal |

Mechanical Installation

Dimensions

SC Series Module Dimensions:

Signal distribution boards are designed according to the user’s needs, and dimensions are described separately.

Backplane Installation Method

①

②

③

Installation Procedure

Cut off power supply

Mount the signal distribution board on the fixed backplane witih screws and isolation posts

Insert predefined AM modules according to mechanical code

- Part specification:

  - Isolation column (1,2,3,4,5,6)

    - Specification:M4*7*5(mm)

    - Quantity: depends on the type of signal distribution boards

  - Set screw (7,8,9,10,11,12)

    - Specification:M4*10(mm)

  - Quantity: depends on the type of signal distribution boards

  - Signal distribution board (13,14)

    - Signal distribution boards are designed according to requirements, the figure shows AM-8012 general-purpose signal distribution boards

Rail Installation Method

①

②

③

Installation Procedure

①Cut off power supply

②Mount the module holder that fixes the base plate on 35mm DIN rail.

③Insert the predefined AM module according to mechanical code.

Note:  1 and 2 are illustrated by AM-8012-0800 signal distribution board.

Mechanical Position Coding

SC series power supply and I/O modules have two signal-specific mechanical positioning pillars at the bottom, and the corresponding area on the mating signal distribution board has two matching mechanical positioning holes. The positioning pillars (holes) are used for mechanical protection options to prevent incorrect installation of SC modules, reducing the risk of errors during installation. The placeholder module does not have positioning pillars.

Area of positioning coding column

Area of positioning coding hole

Taking the analog output module as an example

Electrical Installation

Power Supply

SC series modules and signal distribution board have separate designs for Us and Up, requiring a separate 24V power supply for both Us and Up.

Power supply A and B respectively supply power to Us and Up

Wiring specifications

Inline spring connections

Wire cross-sectional area:0.2~1.5mm²

AWG specification:24~16AWG

Cross-sectional area of the conductor with casing:0.2~0.75mm²

Strip length:8mm

|  | Prompt |
| --- | --- |
|  | The module’s PE ports are designed as dual ports. For general use, select either port and ground it. When the power supply uses a wire with a shield, connect the shield to the other PE port. |

Wiring specifications

Standard CAT5e Ethernet cable, shielded

Ether CAT Network Connection

Interface definition

| Logo | Description |
| --- | --- |
| EC IN | EtherCAT IN interface connected to master or preceding stage slaves |
| EC OUT | EtherCAT OUT interface connected to post stage slave station |

Pin Definition

| Pin | Name | Description |
| --- | --- | --- |
| 1 | Tx+ | EtherCAT data transmission, differential signaling + |
| 2 | Tx- | EtherCAT data transmission, with differential signaling - |
| 3 | Rx+ | EtherCAT data reception, differential signaling+ |
| 6 | Rx- | EtherCAT data reception, differential signaling - |
| 4, 5, 7, 8 | - | Not used |

Indicator

| Logo | Object | Color | Description |
| --- | --- | --- | --- |
| ECAT RUN | EtherCAT Status | Yellow | On: the device is in an operable state 1s flash: in the ready state, can not be operated 0.5s flash: in safe state, no output operation is allowed |
| ECAT ERR | EtherCAT Communication Errors | Yellow | On: Error in slave device communication |
| ECAT IN LinkACT | IN port communication link status | Green | On: link established with preceding stage module Flash: Establish communication with the preceding stage module |
| ECAT OUT LinkACT | OUT port communication link status | Green | On: link established with the post stage module Flash: establish communication with the post stage module |

Ether CAT Bus Topology

MC slave 1

Main station

MC slave 2

MC slave n

- When the SC module group is the first slave device group connected to the master, it must be connected to the master with EC IN port on the module signal distribution board.

- When the SC module group is the slave device in the middle position, it must be connected to the former slave device with EC IN port and to the latter slave device with EC OUT port.

- When the module is the last slave device, it must be connected to the preceding stage slave device with EC IN port and vacate EC OUT port.

Input and Output Signals

NPN-type input

NPN-type input

NPN-type input

PNP-type input

PNP -type input

PNP -type input

NPN sensors

NPN-type output

NPN-type output

PNP -type output

PNP -type output

2-wire connection

Single-wire connection

Single-wire connection

Single-wire connection

Single-wire connection

2-wire connection

2-wire connection

3-wire connection

3-wire connection

2-wire connection

AI analog output

AI analog input

PNP sensors

EtherCAT Communication

  - About EtherCAT

EtherCAT Introduction

EtherCAT (Ethernet Control Automation Technology) is an Ethernet-based fieldbus system in which I/O data is exchanged at a speed of 100 MBit/s in full-duplex mode and the delay of messages is controlled in μs compared to conventional Ethernet communication.

The EtherCAT protocol, optimized for process data, transmits directly in Ethernet telegrams, which in turn consists of multiple sub-telegrams, each of which runs in the storage area of the process image.

Since each EtherCAT gateway is provided with an unambiguous address (MAC address), the data-related order is independent of the physical order of the EtherCAT gateways in the network.

EtherCAT State Machine

The status of each EtherCAT slave is controlled via the EtherCAT State Machine (ESM) of the master guide slave. This allows different functions to be accessed or performed in the EtherCAT slave.

| State | Description |
| --- | --- |
| Boot | The firmware of the slave can be updated, and the boot state can only be switched from the init state Mailbox communication can only be used for FoE, and other mailbox protocols and process communication are not available |
| Init | The powered-on slave is in an initialized state. No mailbox can communicate with process data The master initializes the synchronization manager channels 0 and 1 for the mailbox communication |
| Pre-OP | During the Init switch to Pre-OP state, the slave will check whether the mailbox is initialized correctly. In the Pre-OP state, mailbox communication is possible, but process data communication is not possible. The master will initialize the synchronization manager channel for process data, FMMU channel and PDO mapping. |
| S-OP | During switching Pre-OP to S-OP, the slave checks whether the mailbox is initialized correctly. In the S-OP state, mailbox communication can be carried out, but process data communication is not possible, and the master will initialize the synchronization manager channel, FMMU channel, PDO mapping and PDO assignment for the process data |
| OP | In the OP state, the slave assigns the output data from the master to its own output port Process data and mailbox communication can be carried out normally. |

CoE Interface

CoE interface (CANopen over EtherCAT) is used for parameter management of EtherCAT devices.  EtherCAT slave or master manages constants (read-only) or variables for operation, diagnostics, commissioning, and so on. CoE parameters are assigned in a hierarchical form, and in principle, the user only has access to read through the bus. The EtherCAT master has access to the slave’s local CoE parameter list in read-write mode.

There are different data types for CoE parameters: String, integer, BOOL, and field, which can be used to describe a wide range of features. For example, Vendor ID, serial number, process data settings, device name, calibration value of analog signal, or password information.

All instructions are defined as 2 levels by hexadecimal numbers: Index and SubIndex, with a range of values:

Index: 0x0000 ...... 0xFFFF(0 …… 65535dec)

SubIndex: 0x00 ...... 0xFF(0 ……  255dec)

Local parameters are generally expressed as 0x8010:0A, 0x is defined as a hexadecimal number, and colons are used to distinguish between an index and a subindex

|  | Prompt |
| --- | --- |
|  | Not every EtherCAT slave has a CoE list. Some simple processorless I/O modules have no parameter variables, so there are no CoE parameter tables |

List of CoEs for slaves:

Distributed Clock

A distributed clock represents a local clock in an EtherCAT slave controller (ESC) that has the following characteristics:

-  1 ns resolution unit

-  Zero point

-  64-bit chronograph for 584 years (32-bit chronograph for 4.2 seconds)

-  The EtherCAT master automatically synchronizes the local clock with the master clock with an accuracy of < 100 ns

EtherCAT Parameters of Analog I/O Modules

4 | 8-channel, -10…10V (16bit) Analog Input Module

PDO process data object parameters

Process data object list PDO List (4 channels: 1≤n≤4, 8 channels: 1≤n≤8)

| Index(hex) | Name | Description | Size(Byte) |
| --- | --- | --- | --- |
| 1A0(2*n-2) | AI Standard Channel n | Analog input standard channel n | 4.0 |
| 1A0(2*n-1) | AI Compact Channel n | Analog input compact channel n | 2.0 |

Process data object contents PDO Content(0x1A0(2*n-2))

| Index(hex) | Name | Description | Offset(Byte) | Data type | Size(Byte) |
| --- | --- | --- | --- | --- | --- |
| 60n0:01 | Status_Underrange | Status Bit – The input value is below the lower limit of measurement | 0.0 | BIT | 0.1 |
| 60n0:02 | Status_Overrange | Status Bits – The input value exceeds the upper limit of the measurement | 0.1 | BIT | 0.1 |
| 60n0:03 | Status_Limit 1 | Limit 1 status bit | 0.2 | BIT2 | 0.2 |
| 60n0:05 | Status_Limit 2 | Limit 2 status bit | 0.4 | BIT2 | 0.2 |
| 60n0:07 | Status_Error | Error status bit | 0.6 | BIT | 0.1 |
|  | --- | Undefined | 0.7 |  | 0.1 |
|  | --- | Undefined | 1.0 |  | 0.6 |
| 60n0:0F | Status_TxPDO State | Status bit of TxPDO State | 1.6 | BIT | 0.1 |
| 60n0:10 | Status_TxPDO Toggle | Status bit of the TxPDO Toggle | 1.7 | BIT | 0.1 |
| 60n0:11 | Value n | Input value of channel n | 2.0 | INT | 2.0 |
|  |  |  | 4.0 |  |  |

Process data object contents PDO Content(0x1A0(2*n-1))

| Index(hex) | Name | Description | Offset(Byte) | Data type | Size(Byte) |
| --- | --- | --- | --- | --- | --- |
| 60n0:11 | Value n | Input value of channel n | 0.0 | INT | 2.0 |
|  |  |  | 2.0 |  |  |

SDO service data object parameters

0x1000 Device Type

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 1000:0 | Device Type | EtherCAT slave device type | UINT 32 | RO | 00001389 |

0x1008 Device name

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 1008:0 | Device Name | EtherCAT slave device name | String | RO | MC322_ |

0x1009 Hardware version

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 1009:0 | Hardware Version | EtherCAT slave hardware version | String | RO | _ |

0x100A Software Version

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 100A:0 | Software Version | EtherCAT slave software version | String | RO | _ |

0x1018  Slave ID

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 1018:0 | Identity | Used to identify slave information | UINT8 | RO | 04 |
| 1018:01 | Vendor ID | EtherCAT slave Vendor ID | UINT32 | RO | _ |
| 1018:02 | Product Code | EtherCAT slave product ID | UINT32 | RO | _ |
| 1018:03 | Revision | EtherCAT slave revision number | UINT32 | RO | _ |
| 1018:04 | Serial Number | Serial number of EtherCAT slave | UINT32 | RO | _ |

0x60n0*** analog input (4 channels: 0≤n≤3, 8 channels: 0≤n≤7)

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 60n0:0 | AI Input Channel n | Analog input channel n+1 | INT16 | RO | 11 |
| 60n0:01 | Status_Underrange | Status Bit – input value is below the lower limit of measurement | BOOLEAN | RO | 00 |
| 60n0:02 | Status_Overrange | Status Bits – input value exceeds the upper limit of the measurement | BOOLEAN | RO | 00 |
| 60n0:03 | Status_Limit 1 | Limit 1 status bit | BIT2 | RO | 00 |
| 60n0:05 | Status_Limit 2 | Limit 2 status bit | BIT2 | RO | 00 |
| 60n0:07 | Status_Error | Error status bit | BOOLEAN | RO | 00 |
| 60n0:0F | Status_TxPDO State | Status bit of TxPDO State | BOOLEAN | RO | 00 |
| 60n0:10 | Status_TxPDO Toggle | Status bit of TxPDO Toggle | BOOLEAN | RO | 00 |
| 60n0:11 | Value n | Input value of channel n+1 | INT16 | RO | 11 |

0x80n0*** analog input settings (4 channels: 0≤n≤3, 8 channels: 0≤n≤7)

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 80n0:0 | AI Settings Ch. n+1 | Channel N+1 input settings | UINT8 | RO | 0B |
| 80n0:01 | Enable User Calibration | Enables user-set calibration parameters | BOOLEAN | RW | 00 |
| 80n0:02 | Enable Vendor Calibration | Enables the calibration parameters set by the Manufacturer | BOOLEAN | RW | 01 |
| 80n0:04 | Enable Limit 1 | Enable Limit 1 | BOOLEAN | RW | 00 |
| 80n0:05 | Enable Limit 2 | Enable Limit 2 | BOOLEAN | RW | 00 |
| 80n0:07 | User Calibration Offset | The user-calibrated offset value is called by enabling 80n0:01 | INT16 | RW | 0000 |
| 80n0:08 | User Calibration Gain | The user-calibrated gain value is called by enabling 80n0:01 | UINT16 | RW | 4000 |
| 80n0:09 | Limit 1 | Set the first threshold | INT16 | RW | 0000 |
| 80n0:0A | Limit 2 | Set the second threshold | INT16 | RW | 0000 |

0x80nE*** analog input internal data (4 channels: 0≤n≤3, 8 channels: 0≤n≤7)

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 80nE:0 | AI Internal Data Ch. n+1 | Internal data | UINT8 | RO | 01 |
| 80nE:01 | ADC Raw Value | Raw value captured by ADC chip | INT16 | RO | 0000 |

0x80nF*** analog input manufacturer data (4 channels: 0≤n≤3, 8 channels: 0≤n≤7)

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 80nF:0 | AI Manufacturer Data Ch. n+1 | Manufacturer data | UINT8 | RO | 02 |
| 80nF:01 | Calibration Offset | The calibration offset value set by the manufacturer is called by enabling 80n0:02 | INT16 | RW | _ |
| 80nF:02 | Calibration Gain | The gain value set by the manufacturer is called by enabling 80n0:02 | INT16 | RW | _ |

0xF008***Parameter handling

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| F008:0 | Parameter Handling | Parameter handling | INT8 | RO | 04 |
| F008:01 | Save Current Parameters | Save the current set parameters, enter 0x1234 to save parameters, and the value is 0 after the restoration is completed. | UINT16 | RW | 0000 |
| F008:02 | Restore Default Parameters | Restore ex-factory parameters, enter 0x1234 to restore default parameters, and the value is 0 after the restoration is completed | UINT16 | RW | 0000 |
| F008:03 | Checksum | Parameter checksums | UINT16 | RO | _ |
| F008:04 | Manufacturer Reserve | Manufacturer reserved | UINT16 | RW | 0000 |

4 | 8-channel, 0…20mA (16bit) Analog Input Module

PDO Process data object parameters

PDO List (4 channels: 1≤n≤ 4, 8 channels: 1≤n≤8)

| Index(hex) | Name | Description | Size(Byte) |
| --- | --- | --- | --- |
| 1A0(2*n-2) | AI Standard Channel n | Analog input standard channel n | 4.0 |
| 1A0(2*n-1) | AI Compact Channel n | Analog input compact channel n | 2.0 |

Process data object contentsPDO Content(0x1A0(2*n-2))

| Index(hex) | Name | Description | Offset(Byte) | Data type | Size(Byte) |
| --- | --- | --- | --- | --- | --- |
| 60n0:01 | Status_Underrange | Status bit - input value below lower measurement limit | 0.0 | BIT | 0.1 |
| 60n0:02 | Status_Overrange | Status bit - the input value exceeds the upper measurement limit | 0.1 | BIT | 0.1 |
| 60n0:03 | Status_Limit 1 | Limit 1 status bit | 0.2 | BIT2 | 0.2 |
| 60n0:05 | Status_Limit 2 | Limit 2 status bit | 0.4 | BIT2 | 0.2 |
| 60n0:07 | Status_Error | Error status bit | 0.6 | BIT | 0.1 |
|  | --- | Undefined | 0.7 |  | 0.1 |
|  | --- | Undefined | 1.0 |  | 0.6 |
| 60n0:0F | Status_TxPDO State | TxPDO State status bit | 1.6 | BIT | 0.1 |
| 60n0:10 | Status_TxPDO Toggle | TxPDO Toggle Status Bit | 1.7 | BIT | 0.1 |
| 60n0:11 | Value n | Input value of channel n | 2.0 | INT | 2.0 |
|  |  |  | 4.0 |  |  |

Process data object contents PDO Content(0x1A0(2*n-1))

| Index(hex) | Name | Description | Offset (Byte) | Data type | Size(Byte) |
| --- | --- | --- | --- | --- | --- |
| 60n0:11 | Value n | Input value of channel n | 0.0 | INT | 2.0 |
|  |  |  | 2.0 |  |  |

SDO Service data object parameters

0x1000 Device type

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 1000:0 | Device Type | EtherCAT slave device type | UINT 32 | RO | 00001389 |

0x1008 Device name

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 1008:0 | Device Name | EtherCAT slave device name | String | RO | MC342_ |

0x1009 Hardware version

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 1009:0 | Hardware Version | EtherCAT slave hardware version | String | RO | _ |

0x100A Software version

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 100A:0 | Software Version | EtherCAT slave software version | String | RO | _ |

0x1018  Slave ID

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 1018:0 | Identity | Used to identify slave information | UINT8 | RO | 04 |
| 1018:01 | Vendor ID | EtherCAT slave Vendor ID | UINT32 | RO | _ |
| 1018:02 | Product Code | EtherCAT slave product ID | UINT32 | RO | _ |
| 1018:03 | Revision | EtherCAT slave revision number | UINT32 | RO | _ |
| 1018:04 | Serial Number | Serial number of the EtherCAT slave | UINT32 | RO | _ |

0x60n0*** analog input (4 channels: 0≤n≤3, 8 channels: 0≤n≤7)

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 60n0:0 | AI Input Channel n | Analog input channel n+1 | INT16 | RO | 11 |
| 60n0:01 | Status_Underrange | Status Bit – The input value is below the lower limit of measurement | BOOLEAN | RO | 00 |
| 60n0:02 | Status_Overrange | Status Bits – The input value exceeds the upper limit of the measurement | BOOLEAN | RO | 00 |
| 60n0:03 | Status_Limit 1 | Limit 1 status bit | BIT2 | RO | 00 |
| 60n0:05 | Status_Limit 2 | Limit 2 status bit | BIT2 | RO | 00 |
| 60n0:07 | Status_Error | Error status bit | BOOLEAN | RO | 00 |
| 60n0:0F | Status_TxPDO State | Status bit of TxPDO State | BOOLEAN | RO | 00 |
| 60n0:10 | Status_TxPDO Toggle | Status bit of the TxPDO Toggle | BOOLEAN | RO | 00 |
| 60n0:11 | Value n | Input value for channel n+1 | INT16 | RO | 11 |

0x80n0*** analog input settings (4 channels: 0≤n≤3, 8 channels: 0≤n≤7)

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 80n0:0 | AI Settings Ch. n+1 | Channel N+1 input settings | UINT8 | RO | 0B |
| 80n0:01 | Enable User Calibration | Enables user-set calibration parameters | BOOLEAN | RW | 00 |
| 80n0:02 | Enable Vendor Calibration | Enables the calibration parameters set by the Manufacturer | BOOLEAN | RW | 01 |
| 80n0:04 | Enable Limit 1 | Enable Limit 1 | BOOLEAN | RW | 00 |
| 80n0:05 | Enable Limit 2 | Enable Limit 2 | BOOLEAN | RW | 00 |
| 80n0:07 | User Calibration Offset | The user-calibrated offset value is called by enabling 80n0:01 | INT16 | RW | 0000 |
| 80n0:08 | User Calibration Gain | The user-calibrated gain value is called by enabling 80n0:01 | UINT16 | RW | 4000 |
| 80n0:09 | Limit 1 | Set the first threshold | INT16 | RW | 0000 |
| 80n0:0A | Limit 2 | Set the second threshold | INT16 | RW | 0000 |

0x80nE*** analog input internal data (4 channels: 0≤n≤3, 8 channels: 0≤n≤7)

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 80nE:0 | AI Internal Data Ch. n+1 | Internal Data | UINT8 | RO | 01 |
| 80nE:01 | ADC Raw Value | The raw value acquired by the ADC chip | INT16 | RO | 0000 |

0x80nF*** analog input Manufacturer data (4 channels: 0≤n≤3, 8 channels: 0≤n≤7)

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 80nF:0 | AI Manufacturer Data Ch. n+1 | Manufacturer data | UINT8 | RO | 02 |
| 80nF:01 | Calibration Offset | The calibration offset value set by the manufacturer is called by enabling 80n0:02 | INT16 | RW | _ |
| 80nF:02 | Calibration Gain | The gain value set by the manufacturer is called by enabling 80n0:02 | INT16 | RW | _ |

0xF008***Parameter handling

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| F008:0 | Parameter Handling | Parameter handling | INT8 | RO | 04 |
| F008:01 | Save Current Parameters | Save the current parameters, enter 0x1234 to save parameters, and the value is 0 after the restoration is completed. | UINT16 | RW | 0000 |
| F008:02 | Restore Default Parameters | Restore ex-factory parameters, enter 0x1234 to restore default parameters, and the value is 0 after the restoration is completed | UINT16 | RW | 0000 |
| F008:03 | Checksum | Parameter checksums | UINT16 | RO | _ |
| F008:04 | Manufacturer Reserve | Manufacturer reserved | UINT16 | RW | 0000 |

4 | 8-channel, 4…20mA (16bit) Analog Input Module

PDO Process data object parameters

PDO List (4 channels: 1≤n≤4, 8 channels: 1≤n≤8)

| Index(hex) | Name | Description | Size(Byte) |
| --- | --- | --- | --- |
| 1A0(2*n-2) | AI Standard Channel n | Analog input standard channel n | 4.0 |
| 1A0(2*n-1) | AI Compact Channel n | Analog input compact channel n | 2.0 |

Process data object contents PDO Content(0x1A0(2*n-2))

| Index(hex) | Name | Description | Offset (Byte) | Data type | Size (Byte) |
| --- | --- | --- | --- | --- | --- |
| 60n0:01 | Status_Underrange | Status Bit – The input value is below the lower limit of measurement | 0.0 | BIT | 0.1 |
| 60n0:02 | Status_Overrange | Status Bits – The input value exceeds the upper limit of the measurement | 0.1 | BIT | 0.1 |
| 60n0:03 | Status_Limit 1 | Limit 1 status bit | 0.2 | BIT2 | 0.2 |
| 60n0:05 | Status_Limit 2 | Limit 2 status bit | 0.4 | BIT2 | 0.2 |
| 60n0:07 | Status_Error | Error status bit | 0.6 | BIT | 0.1 |
|  | --- | Undefined | 0.7 |  | 0.1 |
|  | --- | Undefined | 1.0 |  | 0.6 |
| 60n0:0F | Status_TxPDO State | Status bit of TxPDO State | 1.6 | BIT | 0.1 |
| 60n0:10 | Status_TxPDO Toggle | Status bit of the TxPDO Toggle | 1.7 | BIT | 0.1 |
| 60n0:11 | Value n | Input value of channel n | 2.0 | INT | 2.0 |
|  |  |  | 4.0 |  |  |

Process data object contents PDO Content(0x1A0(2*n-1))

| Index(hex) | Name | Description | Offset(Byte) | Data type | Size(Byte) |
| --- | --- | --- | --- | --- | --- |
| 60n0:11 | Value n | Input value of channel n | 0.0 | INT | 2.0 |
|  |  |  | 2.0 |  |  |

SDO Service data object parameters

0x1000 Device type

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 1000:0 | Device Type | EtherCAT slave device type | UINT 32 | RO | 00001389 |

0x1008 Device name

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 1008:0 | Device Name | EtherCAT slave device name | String | RO | MC342_ |

0x1009 Hardware version

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 1009:0 | Hardware Version | EtherCAT slave hardware version | String | RO | _ |

0x100A Software version

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 100A:0 | Software Version | EtherCAT slave software version | String | RO | _ |

0x1018  Slave ID

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 1018:0 | Identity | Used to identify slave information | UINT8 | RO | 04 |
| 1018:01 | Vendor ID | EtherCAT slave Vendor ID | UINT32 | RO | _ |
| 1018:02 | Product Code | EtherCAT slave product ID | UINT32 | RO | _ |
| 1018:03 | Revision | EtherCAT slave revision number | UINT32 | RO | _ |
| 1018:04 | Serial Number | Serial number of the EtherCAT slave | UINT32 | RO | _ |

0x60n0*** analog input (4 channels: 0≤n≤3, 8 channels: 0≤n≤7)

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 60n0:0 | AI Input Channel n | Analog input channel n+1 | INT16 | RO | 11 |
| 60n0:01 | Status_Underrange | Status Bit – The input value is below the lower limit of measurement | BOOLEAN | RO | 00 |
| 60n0:02 | Status_Overrange | Status Bits – The input value exceeds the upper limit of the measurement | BOOLEAN | RO | 00 |
| 60n0:03 | Status_Limit 1 | Limit 1 status bit | BIT2 | RO | 00 |
| 60n0:05 | Status_Limit 2 | Limit 2 status bit | BIT2 | RO | 00 |
| 60n0:07 | Status_Error | Error status bit | BOOLEAN | RO | 00 |
| 60n0:0F | Status_TxPDO State | Status bit of TxPDO State | BOOLEAN | RO | 00 |
| 60n0:10 | Status_TxPDO Toggle | Status bit of TxPDO Toggle | BOOLEAN | RO | 00 |
| 60n0:11 | Value n | Input value for channel n+1 | INT16 | RO | 11 |

0x80n0*** analog input settings (4 channels: 0≤n≤3, 8 channels: 0≤n≤7)

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 80n0:0 | AI Settings Ch. n+1 | Channel N+1 input settings | UINT8 | RO | 0B |
| 80n0:01 | Enable User Calibration | Enables user-set calibration parameters | BOOLEAN | RW | 00 |
| 80n0:02 | Enable Vendor Calibration | Enables the calibration parameters set by the Manufacturer | BOOLEAN | RW | 01 |
| 80n0:04 | Enable Limit 1 | Enable Limit 1 | BOOLEAN | RW | 00 |
| 80n0:05 | Enable Limit 2 | Enable Limit 2 | BOOLEAN | RW | 00 |
| 80n0:07 | User Calibration Offset | The user-calibrated offset value is called by enabling 80n0:01 | INT16 | RW | 0000 |
| 80n0:08 | User Calibration Gain | The user-calibrated gain value is called by enabling 80n0:01 | UINT16 | RW | 4000 |
| 80n0:09 | Limit 1 | Set the first threshold | INT16 | RW | 0000 |
| 80n0:0A | Limit 2 | Set the second threshold | INT16 | RW | 0000 |

0x80nE*** analog input internal data (4 channels: 0≤n≤3, 8 channels: 0≤n≤7)

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 80nE:0 | AI Internal Data Ch. n+1 | Internal Data | UINT8 | RO | 01 |
| 80nE:01 | ADC Raw Value | The raw value acquired by the ADC chip | INT16 | RO | 0000 |

0x80nF*** analog input Manufacturer data (4 channels: 0≤n≤3, 8 channels: 0≤n≤7)

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 80nF:0 | AI Manufacturer Data Ch. n+1 | Manufacturer data | UINT8 | RO | 02 |
| 80nF:01 | Calibration Offset | The calibration offset value set by the manufacturer is called by enabling 80n0:02 | INT16 | RW | _ |
| 80nF:02 | Calibration Gain | The gain value set by the manufacturer is called by enabling 80n0:02 | INT16 | RW | _ |

0xF008***Parameter handling

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| F008:0 | Parameter Handling | Parameter handling | INT8 | RO | 04 |
| F008:01 | Save Current Parameters | Save the current set parameters, enter 0x1234 to save parameters, and the value is 0 after the restoration is completed. | UINT16 | RW | 0000 |
| F008:02 | Restore Default Parameters | Restore ex-factory parameters, enter 0 x 1234 to restore default parameters, and the value is 0 after the restoration is completed. | UINT16 | RW | 0000 |
| F008:03 | Checksum | Parameter checksums | UINT16 | RO | _ |
| F008:04 | Manufacturer Reserve | Manufacturer reserved | UINT16 | RW | 0000 |

4-channel, -10…10V (16bit) Analog Output Module

PDO Process data object parameters

PDO List (4 channels: 0≤n≤3)

| Index(hex) | Name | Description | Size(Byte) |
| --- | --- | --- | --- |
| 1A00 | AO Status | Analog output status word | 2.0 |
| 160n | AO Output Channel n+1 | Analog output N+1 channel | 2.0 |

Process data object contents PDO Content(0x1A00)

| Index(hex) | Name | Description | Offset(Byte) | Data type | Size(Byte) |
| --- | --- | --- | --- | --- | --- |
| 6000:01 | Status_Temp error | Temperature alarm status bit | 0.0 | BIT | 0.1 |
| 60n0:02 | Status_Fault field voltage | Abnormal voltage alarm status bit on the field side | 0.1 | BIT | 0.1 |
| 60n0:03 | Status_Fault DAC | 1-4 channel alarm status bits | 0.2 | BIT | 0.1 |
|  | --- |  | 0.3 |  | 0.5 |
| 60n0:09 | Status_Error Ch. 1 | 1- channel alarm status bit | 1.0 | BIT | 0.1 |
| 60n0:0A | Status_Error Ch. 2 | 2-channel alarm status bits | 1.1 | BIT | 0.1 |
| 60n0:0B | Status_Error Ch. 3 | 3-channel alarm status bits | 1.2 | BIT | 0.1 |
| 60n0:0C | Status_Error Ch. 4 | 4-channel alarm status bits | 1.3 | BIT | 0.1 |
| 60n0:0D | Status_Diag | The error log status bit is cleared to zero in case of power outrage | 1.4 | BIT | 0.1 |
|  | --- |  | 1.5 |  | 0.3 |
|  |  |  | 2.0 |  |  |

Process data object contents PDO Content(0x160n)0≤n≤3

| Index(hex) | Name | Description | Offset(Byte) | Data type | Size(Byte) |
| --- | --- | --- | --- | --- | --- |
| 70n0:01 | Analog Output n+1 | Channel n+1 output value | 0.0 | INT | 2.0 |
|  |  |  | 2.0 |  |  |

SDO Service Data Object Parameters

0x1000 Device Type

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 1000:0 | Device Type | EtherCAT slave device type | UINT 32 | RO | 00001389 |

0x1008 Device Name

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 1008:0 | Device Name | EtherCAT slave device name | String | RO | MC4224 |

0x1009 Hardware Version

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 1009:0 | Hardware Version | EtherCAT slave hardware version | String | RO | _ |

0x100A Software Version

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 100A:0 | Software Version | EtherCAT slave software version | String | RO | _ |

0x1018 Slave ID

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 1018:0 | Identity | Used to identify slave information | UINT8 | RO | 04 |
| 1018:01 | Vendor ID | EtherCAT slave Vendor ID | UINT32 | RO | _ |
| 1018:02 | Product Code | EtherCAT slave product ID | UINT32 | RO | _ |
| 1018:03 | Revision | EtherCAT slave revision number | UINT32 | RO | _ |
| 1018:04 | Serial Number | Serial number of the EtherCAT slave | UINT32 | RO | _ |

0x6000***Status words (4 channels: 0≤n≤3)

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 6000:0 | Status | Status | UINT8 | RO | 0D |
| 6000:01 | Status_Temp error | Temperature alarm status bit (1: alarm, 0: no alarm) | BOOLEAN | RO | 00 |
| 6000:02 | Status _Fault field voltage | Abnormal voltage alarm status bit on the field side (Up) (1: alarm, 0: no alarm) | BOOLEAN | RO | 00 |
| 6000:03 | Status_Fault DAC | 1-4 channel alarm status bits (1: alarm, 0: no alarm) | BOOLEAN | RO | 00 |
| 6000:09 | Status_Error CH.1 | 1- channel alarm status bit (1: alarm, 0: no alarm) | BOOLEAN | RO | 00 |
| 6000:0A | Status_Error CH.2 | 2-channel alarm status bit (1: alarm, 0: no alarm) | BOOLEAN | RO | 00 |
| 6000:0B | Status_Error CH.3 | 3-channel alarm status bit (1: alarm, 0: no alarm) | BOOLEAN | RO | 00 |
| 6000:0C | Status_Error CH.4 | 4-channel alarm status bit (1: alarm, 0: no alarm) | BOOLEAN | RO | 00 |
| 6000:0D | Status_Diag | Error record, 1 after the error occurs, 0 in case of power outrage. | BOOLEAN | RO | 00 |

0x70n0***Analog output settings (4 channels: 0≤n≤3)

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 70n0:0 | AO Outputs Ch. n+1 | Analog output N+1 channel | UINT8 | RO | 01 |
| 70n0:01 | Analog Output | Analog output data | INT16 | RO | 0000 |

0x80n0***Analog output setting (4 channels: 0≤n≤3)

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 80n0:0 | AO Settings Ch. n+1 | Analog output setting | UINT8 | RO | 16 |
| 80n0:01 | Enable User Calibration | Enable user calibration | BOOLEAN | RW | 00 |
| 80n0:02 | Enable Vendor Calibration | Enable vendor calibration | BOOLEAN | RW | 01 |
| 80n0:03 | Watchdog | 0: the default value (0x80n0:06) is directly output if the watchdog is overtime. 1: if the watchdog is over time, increment to the default output value at digits/ms (0x80n0:07). 2: After the watchdog is overtime, the last valid data is output. | BIT2 | RW | 00 |
| 80n0:06 | Default Output | Default output value | INT16 | RW | 0000 |
| 80n0:07 | Default Output Ramp | The rate at which the output is to the default value, in digits/ms | UINT16 | RW | FFFF |
| 80n0:08 | User Calibration Offset | The offset value of the user calibration | INT16 | RW | 0000 |
| 80n0:09 | User Calibration Gain | The user-calibrated gain value | UINT16 | RW | FFFF |

0x80nE***Analog output of internal data (4 channels:0≤n≤3)

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 80nE:0 | AO Internal Data Ch. n+1 | Analog output n+1 channel internal data | UINT8 | RO | 01 |
| 80nE:01 | DAC Raw Value | Calibration value output to DAC chip | INT16 | RO | 0000 |

0x80nF*** analog output manufacturer data (4 channels: 0≤n≤3)

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 80nF:0 | AO Manufacturer Data Ch. n+1 | Analog output of N+1 channel manufacturer data | UINT8 | RO | 02 |
| 80nF:01 | Calibration Offset | The calibration offset value set by the manufacturer is called by enabling 80n0:02 | INT16 | RW | _ |
| 80nF:02 | Calibration Gain | The gain offset value set by the manufacturer is called by enabling 80n0:02 | UINT16 | RW | _ |

0xF008***Parameter handling

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| F008:0 | Parameter Handling | Parameter handling | INT8 | RO | 04 |
| F008:01 | Save Current Parameters | Save the current set parameters, enter 0x1234 to save the parameters, and the value is 0 after saving is completed. | UINT16 | RW | 0000 |
| F008:02 | Restore Default Parameters | Restore ex-factory parameters, enter 0 x 1234 to restore default parameters, and the value is 0 after the restoration is completed. | UINT16 | RW | 0000 |
| F008:03 | Checksum | Parameter checksums | UINT16 | RO | _ |
| F008:04 | Manufacturer Reserve | Manufacturer reserved | UINT16 | RW | 0000 |

4-channel, 0…20mA (16bit) Analog Output Module

PDO Process data object parameters

PDO List (4 channels: 0≤n≤3)

| Index(hex) | Name | Description | Size (Byte) |
| --- | --- | --- | --- |
| 1A00 | AO Status | Analog output status word | 2.0 |
| 160n | AO Output Channel n | Analog output N+1 channel | 2.0 |

Process data object contents PDO Content(0x1A00)

| Index(hex) | Name | Description | Offset (Byte) | Data type | Size (Byte) |
| --- | --- | --- | --- | --- | --- |
| 6000:01 | Status_Temp error | Temperature alarm status bit | 0.0 | BIT | 0.1 |
| 60n0:02 | Status_Fault field voltage | Abnormal voltage alarm status bit on the field side | 0.1 | BIT | 0.1 |
| 60n0:03 | Status_Fault DAC | 1-4 channel alarm status bits | 0.2 | BIT | 0.1 |
|  | --- |  | 0.3 |  | 0.5 |
| 60n0:09 | Status_N/A1 | 1- channel alarm status bit | 1.0 | BIT | 0.1 |
| 60n0:0A | Status_N/A2 | 2-channel alarm status bits | 1.1 | BIT | 0.1 |
| 60n0:0B | Status_ N/A3 | 3-channel alarm status bits | 1.2 | BIT | 0.1 |
| 60n0:0C | Status_ N/A4 | 4-channel alarm status bits | 1.3 | BIT | 0.1 |
| 60n0:0D | Status_Diag | The error log status bit is cleared to zero in case of power outrage | 1.4 | BIT | 0.1 |
|  | --- |  | 1.5 |  | 0.3 |
|  |  |  | 2.0 |  |  |

Process data object contents PDO Content(0x160n) 0≤n≤3

| Index(hex) | Name | Description | Offset (Byte) | Data type | Size (Byte) |
| --- | --- | --- | --- | --- | --- |
| 70n0:01 | Analog Output n+1 | Channel n+1 output value | 0.0 | INT | 2.0 |
|  |  |  | 2.0 |  |  |

SDO Service Data Object Parameters

0x1000 Device Type

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 1000:0 | Device Type | EtherCAT slave device type | UINT 32 | RO | 00001389 |

0x1008 Device Name

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 1008:0 | Device Name | EtherCAT slave device name | String | RO | MC4424 |

0x1009 Hardware Version

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 1009:0 | Hardware Version | EtherCAT slave hardware version | String | RO | _ |

0x100A Software Version

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 100A:0 | Software Version | EtherCAT slave software version | String | RO | _ |

0x1018 Slave ID

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 1018:0 | Identity | Used to identify slave information | UINT8 | RO | 04 |
| 1018:01 | Vendor ID | EtherCAT slave Vendor ID | UINT32 | RO | _ |
| 1018:02 | Product Code | EtherCAT slave product ID | UINT32 | RO | _ |
| 1018:03 | Revision | EtherCAT slave revision number | UINT32 | RO | _ |
| 1018:04 | Serial Number | Serial number of the EtherCAT slave | UINT32 | RO | _ |

0x6000*** status word (4 channels: 0≤n≤3)

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 6000:0 | Status | Status | UINT8 | RO | 0D |
| 6000:01 | Status_Temp error | Temperature alarm status bit (1: alarm, 0: no alarm) | BOOLEAN | RO | 00 |
| 6000:02 | Status _Fault field voltage | Abnormal voltage alarm status bit on the field side (Up) (1: alarm, 0: no alarm) | BOOLEAN | RO | 00 |
| 6000:03 | Status_Fault DAC | 1-4 channel alarm status bits (1: alarm, 0: no alarm) | BOOLEAN | RO | 00 |
| 6000:09 | Status_ N/A 1 | 1-channel alarm status bit (1: alarm, 0: no alarm) | BOOLEAN | RO | 00 |
| 6000:0A | Status_ N/A 2 | 2-channel alarm status bit (1: alarm, 0: no alarm) | BOOLEAN | RO | 00 |
| 6000:0B | Status_ N/A 3 | 3-channel alarm status bit (1: alarm, 0: no alarm) | BOOLEAN | RO | 00 |
| 6000:0C | Status_ N/A 4 | 4-channel alarm status bit (1: alarm, 0: no alarm) | BOOLEAN | RO | 00 |
| 6000:0D | Status_Diag | Error record, 1 after the error occurs, 0 will be cleared in case of power outrage. | BOOLEAN | RO | 00 |

0x70n0*** analog output setting (4 channels: 0≤n≤3)

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 70n0:0 | AO Outputs Ch. n+1 | Analog output n+1 channel | UINT8 | RO | 01 |
| 70n0:01 | Analog Output | Analog output data | INT16 | RO | 0000 |

0x80n0*** analog output setting (4 channels: 0≤n≤3)

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 80n0:0 | AO Settings Ch. n+1 | Analog output setting | UINT8 | RO | 16 |
| 80n0:01 | Enable User Calibration | Enable user calibration | BOOLEAN | RW | 00 |
| 80n0:02 | Enable Vendor Calibration | Enable vendor calibration | BOOLEAN | RW | 01 |
| 80n0:03 | Watchdog | 0: After the watchdog is overtime, the default value (0x80n0:06) is directly output. 1: After the watchdog is overtime, increment to the default output value at digits/ms (0x80n0:07). 2: After the watchdog is overtime, the last valid data is output. | BIT2 | RW | 00 |
| 80n0:06 | Default Output | Default output value | INT16 | RW | 0000 |
| 80n0:07 | Default Output Ramp | The rate at which the output is to the default value, in digits/ms | UINT16 | RW | FFFF |
| 80n0:08 | User Calibration Offset | The offset value of the user calibration | INT16 | RW | 0000 |
| 80n0:09 | User Calibration Gain | The user-calibrated gain value | UINT16 | RW | FFFF |

0x80nE*** analog output internal data (4 channels: 0≤n≤3)

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 80nE:0 | AO Internal Data Ch. n+1 | Analog output N+1 channel internal data | UINT8 | RO | 01 |
| 80nE:01 | DAC Raw Value | The calibration value output to DAC chip | INT16 | RO | 0000 |

0x80nF*** analog output manufacturer data (4 channels: 0≤n≤3)

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 80nF:0 | AO Manufacturer Data Ch. n+1 | Analog output of n+1 channel Manufacturer data | UINT8 | RO | 02 |
| 80nF:01 | Calibration Offset | The calibration offset value set by the manufacturer is called by enabling 80n0:02 | INT16 | RW | _ |
| 80nF:02 | Calibration Gain | The gain offset value set by the manufacturer is called by enabling 80n0:02 | UINT16 | RW | _ |

0xF008***Parameter handling

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| F008:0 | Parameter Handling | Parameter handling | INT8 | RO | 04 |
| F008:01 | Save Current Parameters | Save the current set parameters, enter 0 x1234 to save the parameters, and the value is 0 after saving is completed. | UINT16 | RW | 0000 |
| F008:02 | Restore Default Parameters | Restore ex-factory parameters, enter 0 x 1234 to restore default parameters, and the value is 0 after the restoration is completed. | UINT16 | RW | 0000 |
| F008:03 | Checksum | Parameter checksums | UINT16 | RO | _ |
| F008:04 | Manufacturer Reserve | Manufacturer reserved | UINT16 | RW | 0000 |

4-channel, 4…20mA (16bit) Analog Output Module

PDO Process data object parameters

PDO List (4 channels: 0≤n≤3)

| Index(hex) | Name | Description | Size (Byte) |
| --- | --- | --- | --- |
| 1A00 | AO Status | Analog output status word | 2.0 |
| 160n | AO Output Channel n | Analog output N+1 channel | 2.0 |

Process data object contents PDO Content(0x1A00)

| Index(hex) | Name | Description | Offset (Byte) | Data type | Size (Byte) |
| --- | --- | --- | --- | --- | --- |
| 6000:01 | Status_Temp error | Temperature alarm status bit | 0.0 | BIT | 0.1 |
| 60n0:02 | Status_Fault field voltage | Abnormal voltage alarm status bit on the field side | 0.1 | BIT | 0.1 |
| 60n0:03 | Status_Fault DAC | 1-4 channel alarm status bits | 0.2 | BIT | 0.1 |
|  | --- |  | 0.3 |  | 0.5 |
| 60n0:09 | Status_N/A1 | 1-channel alarm status bit | 1.0 | BIT | 0.1 |
| 60n0:0A | Status_N/A2 | 2-channel alarm status bits | 1.1 | BIT | 0.1 |
| 60n0:0B | Status_ N/A3 | 3-channel alarm status bits | 1.2 | BIT | 0.1 |
| 60n0:0C | Status_ N/A4 | 4-channel alarm status bits | 1.3 | BIT | 0.1 |
| 60n0:0D | Status_Diag | The error log status bit is cleared to zero in case of power outrage. | 1.4 | BIT | 0.1 |
|  | --- |  | 1.5 |  | 0.3 |
|  |  |  | 2.0 |  |  |

Process data object contents PDO Content(0x160n)0≤n≤3)

| Index(hex) | Name | Description | Offset (Byte) | Data type | Size (Byte) |
| --- | --- | --- | --- | --- | --- |
| 70n0:01 | Analog Output n+1 | Channel n+1 output value | 0.0 | INT | 2.0 |
|  |  |  | 2.0 |  |  |

SDO Service data object parameters

0x1000 Device Type

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 1000:0 | Device Type | EtherCAT slave device type | UINT 32 | RO | 00001389 |

0x1008 Device Name

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 1008:0 | Device Name | EtherCAT slave device name | String | RO | MC4524 |

0x1009 Hardware Version

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 1009:0 | Hardware Version | EtherCAT slave hardware version | String | RO | _ |

0x100A Software Version

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 100A:0 | Software Version | EtherCAT slave software version | String | RO | _ |

0x1018 Slave ID

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 1018:0 | Identity | Used to identify slave information | UINT8 | RO | 04 |
| 1018:01 | Vendor ID | EtherCAT slave Vendor ID | UINT32 | RO | _ |
| 1018:02 | Product Code | EtherCAT slave product ID | UINT32 | RO | _ |
| 1018:03 | Revision | EtherCAT slave revision number | UINT32 | RO | _ |
| 1018:04 | Serial Number | Serial number of the EtherCAT slave | UINT32 | RO | _ |

0x6000*** status word (4 channels: 0≤n≤3)

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 6000:0 | Status | Status | UINT8 | RO | 0D |
| 6000:01 | Status_Temp error | Temperature alarm status bit (1: alarm, 0: no alarm) | BOOLEAN | RO | 00 |
| 6000:02 | Status _Fault field voltage | Abnormal voltage alarm status bit on the field side (Up) (1: alarm, 0: no alarm) | BOOLEAN | RO | 00 |
| 6000:03 | Status_Fault DAC | 1-4 channel alarm status bits (1: alarm, 0: no alarm) | BOOLEAN | RO | 00 |
| 6000:09 | Status_ N/A 1 | 1-channel alarm status bit (1: alarm, 0: no alarm) | BOOLEAN | RO | 00 |
| 6000:0A | Status_ N/A 2 | 2-channel alarm status bit (1: alarm, 0: no alarm) | BOOLEAN | RO | 00 |
| 6000:0B | Status_ N/A 3 | 3-channel alarm status bit (1: alarm, 0: no alarm) | BOOLEAN | RO | 00 |
| 6000:0C | Status_ N/A 4 | 4-channel alarm status bit (1: alarm, 0: no alarm) | BOOLEAN | RO | 00 |
| 6000:0D | Status_Diag | Error record, 1 after the error occurs, 0 will be cleared in case of outrage. | BOOLEAN | RO | 00 |

0x70n0*** analog output setting (4 channels: 0≤n≤3)

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 70n0:0 | AO Outputs Ch. n+1 | Analog output n+1 channel | UINT8 | RO | 01 |
| 70n0:01 | Analog Output | Analog output data | INT16 | RO | 0000 |

0x80n0*** analog output setting (4 channels: 0≤n≤3)

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 80n0:0 | AO Settings Ch. n+1 | Analog output setting | UINT8 | RO | 16 |
| 80n0:01 | Enable User Calibration | Enable user calibration | BOOLEAN | RW | 00 |
| 80n0:02 | Enable Vendor Calibration | Enable vendor calibration | BOOLEAN | RW | 01 |
| 80n0:03 | Watchdog | 0: After the watchdog is overtime, the default value (0x80n0:06) is directly output. 1: After the watchdog is overtime, increment to the default output value at digits/ms (0x80n0:07). 2: After the watchdog is overtime, the last valid data is output. | BIT2 | RW | 00 |
| 80n0:06 | Default Output | Default output value | INT16 | RW | 0000 |
| 80n0:07 | Default Output Ramp | The rate at which the output is to the default value, in digits/ms | UINT16 | RW | FFFF |
| 80n0:08 | User Calibration Offset | The offset value of the user calibration | INT16 | RW | 0000 |
| 80n0:09 | User Calibration Gain | The user-calibrated gain value | UINT16 | RW | FFFF |

0x80nE*** analogue output internal data (4 channels: 0≤n≤3)

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 80nE:0 | AO Internal Data Ch. n+1 | Analog output N+1 channel internal data | UINT8 | RO | 01 |
| 80nE:01 | DAC Raw Value | The calibration value output to DAC chip | INT16 | RO | 0000 |

0x80nF*** analog output Manufacturer data (4 channels: 0≤n≤3)

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 80nF:0 | AO Manufacturer Data Ch. n+1 | Analog output of n+1 channel Manufacturer data | UINT8 | RO | 02 |
| 80nF:01 | Calibration Offset | The calibration offset value set by the manufacturer is called by enabling 80n0:02 | INT16 | RW | _ |
| 80nF:02 | Calibration Gain | The gain offset value set by the manufacturer is called by enabling 80n0:02 | UINT16 | RW | _ |

0xF008***Parameter handling

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| F008:0 | Parameter Handling | Parameter handling | INT8 | RO | 04 |
| F008:01 | Save Current Parameters | Save the current set parameters, enter 0x1234 to save the parameters, and the value is 0 after saving is completed. | UINT16 | RW | 0000 |
| F008:02 | Restore Default Parameters | Restore ex-factory parameters, enter 0 x 1234 to restore default parameters, and the value is 0 after the restoration is completed. | UINT16 | RW | 0000 |
| F008:03 | Checksum | Parameter checksums | UINT16 | RO | _ |
| F008:04 | Manufacturer Reserve | Manufacturer reserved | UINT16 | RW | 0000 |

Thermocouple Temperature Acquisition Module

PDO Process data

PDO List (4 channels: 1≤n≤4)

| Index(hex) | Name | Description | Size (Byte) |
| --- | --- | --- | --- |
| 1A0(n-1) | RTD Standard Channel n | RTD input channel n | 4.0 |

Process data object contents PDO Content(0x1A0(n-1))

| Index(hex) | Name | Description | Offset (Byte) | Data type | Size (Byte) |
| --- | --- | --- | --- | --- | --- |
| 60n0:01 | Status_Underrange | Status Bit – The input value is below the lower limit of measurement | 0.0 | BIT | 0.1 |
| 60n0:02 | Status_Overrange | Status Bits – The input value exceeds the upper limit of the measurement | 0.1 | BIT | 0.1 |
| 60n0:03 | Status_Error | Error status bit | 0.2 | BIT | 0.1 |
| 60n0:04 | Status_TxPDO State | Status bit of TxPDO State | 0.3 | BIT | 0.1 |
| 60n0:05 | Status_TxPDO Toggle | Status bit of the TxPDO Toggle | 0.4 | BIT | 0.1 |
| --- | --- | Undefined | 0.5 | - | 1.3 |
| 60n0:07 | Value n | Temperature value unit: 0.1°C | 2.0 | INT | 2.0 |
|  |  |  | 4.0 |  |  |

SDO Service data

0x1000 Device Type

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 1000:0 | Device Type | EtherCAT slave device type | UINT 32 | RO | 00001389 |

0x1008 Device Name

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 1008:0 | Device Name | EtherCAT slave device name | String | RO | MC3614 |

0x1009 Hardware Version

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 1009:0 | Hardware Version | EtherCAT slave hardware version | String | RO | _ |

0x100A Software Version

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 100A:0 | Software Version | EtherCAT slave software version | String | RO | _ |

0x1018 Slave ID

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 1018:0 | Identity | Used to identify slave information | UINT8 | RO | 04 |
| 1018:01 | Vendor ID | EtherCAT slave Vendor ID | UINT32 | RO | _ |
| 1018:02 | Product Code | EtherCAT slave product ID | UINT32 | RO | _ |
| 1018:03 | Revision | EtherCAT slave revision number | UINT32 | RO | _ |
| 1018:04 | Serial Number | Serial number of the EtherCAT slave | UINT32 | RO | _ |

0x60n0*** RTD input (4 channels: 0≤n≤3)

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 60n0:0 | RTD Input Channel n | RTD input channel n+1 | INT16 | RO | 7 |
| 60n0:01 | Status_Underrange | Status Bit – The input value is below the lower limit of measurement | BOOLEAN | RO | 00 |
| 60n0:02 | Status_Overrange | Status Bits – The input value exceeds the upper limit of the measurement | BOOLEAN | RO | 01 |
| 60n0:03 | Status_Error | Error status bit | BOOLEAN | RO | 01 |
| 60n0:04 | Status_TxPDO State | Status bit of TxPDO State | BOOLEAN | RO | 00 |
| 60n0:05 | Status_TxPDO Toggle | Status bit of the TxPDO Toggle | BOOLEAN | RO | 00 |
| 60n0:07 | Value n+1 | Input value for channel n+1 | INT16 | RO | _ |

0x80n0*** RTD input setting (4 channels: 0≤n≤3)

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 80n0:0 | RTD Settings Ch. n+1 | Channel n+1 input settings | UINT8 | RO | 1A |
| 80n0:01 | Enable User Scale | Enable user-set range | BOOLEAN | RW | 00 |
| 80n0:02 | Presentation | Number System | UINT8 | RW | 00 |
| 80n0:0A | Enable User Calibration | Enable user calibration | BOOLEAN | RW | 00 |
| 80n0:0B | Enable Vender Calibration | Enable vendor calibration | BOOLEAN | RW | 01 |
| 80n0:11 | User Scale Offset | User measurement range offset | INT16 | RW | 0000 |
| 80n0:12 | User Scale Gain | User measurement range gain | UINT16 | RW | 4000 |
| 80n0:15 | Filter Settings | Filter settings | UINT16 | RW | 0005 |
| 80n0:17 | User Calibration Offset | User calibrated offset value, invoked by enabling 80n0:01 | INT16 | RW | 0000 |
| 80n0:18 | User Calibration Gain | User calibrated gain value, recalled by enabling 80n0:01 | UINT16 |  | 4000 |
| 80n0:19 | RTD Element | RTD factor | UINT16 |  | 0002 |
| 80n0:1A | Connection Technology | Wiring method | UINT16 |  | 0001 |

0x80nE*** RTD Internal Data (4 channels: 0≤n≤3)

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 80nE:0 | RTD Internal Data Ch. n+1 | Internal data | UINT8 | RO | 03 |
| 80nE:01 | ADC Raw Value | The raw value acquired by the ADC chip | DINT32 | RO | _ |
| 80nE:02 | Resistor Raw Value | Original value of the resistance | UINT16 | RO | 9C40 |
| 80nE:03 | Resistor Calibration Value | Resistance calibration value | UINT16 | RO | 9C40 |

0x80nF***RTD Manufacturer Data (4 channels: 0≤n≤3)

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 80nF:0 | RTD Manufacturer Data Ch. n+1 | Manufacturer data | UINT8 | RO | 04 |
| 80nF:01 | Calibration Offset | The calibration offset value set by the manufacturer is called by enabling 80n0:02 | INT16 | RW | 0 |
| 80nF:02 | Calibration Gain | The gain value set by the manufacturer is called by enabling 80n0:02 | UINT16 | RW | 4000 |
| 80nF:03 | PT1000 Calibration Offset | PT1000 calibration offset value | INT16 | RW | 0 |
| 80nF:04 | PT1000 Calibration Gain | PT1000 calibrated gain value | UINT16 | RW | 4000 |

0x8100*** Manufacturer Data

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 8100:0 | Manufacturer Data | Manufacturer’s Data | INT8 | RO | 02 |
| 8100:01 | PT100 Resistor Offset | PT100 Resistance Offset | INT16 | RW | 0 |
| 8100:02 | PT1000 Resistor Offset | PT1000 Resistance Offset | INT16 | RW | 0 |

0xF008*** Parameter Handling

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| F008:0 | Parameter Handling | Parameter handling | INT8 | RO | 04 |
| F008:01 | Save Current Parameters | Save the current set parameters, enter 0x1234 to save the parameters, and the value is 0 after saving is completed. | UINT16 | RW | 0000 |
| F008:02 | Restore Default Parameters | Restore ex-factory parameters, enter 0 x 1234 to restore default parameters, and the value is 0 after the restoration is completed. | UINT16 | RW | 0000 |
| F008:03 | Checksum | Parameter checksums | UINT16 | RO | _ |
| F008:04 | Manufacturer Reserve | Manufacturer reserved | UINT16 | RW | 0000 |

Encoder Input Acquisition Module EtherCAT Parameters

PDO Process Data

PDO List (2 channels: 0≤n≤1)

| Index(hex) | Name | Description | Size (Byte) |
| --- | --- | --- | --- |
| 1A0n | ENC Status Channel n+1 | Channel n+1 encoder status | 14.0 |
| 160n | ENC Control Channel n+1 | Channel n+1 encoder control | 6.0 |

Process data object contents PDO Content(0x1A0n)

| Index(hex) | Name | Description | Offset (Byte) | Data type | Size (Byte) |
| --- | --- | --- | --- | --- | --- |
| 60n0:01 | Status_Latch Z valid | Status bit—Z-phase latching 1: Valid; 0: invalid | 0.0 | BIT | 0.1 |
| 60n0:02 | Status_Latch extern valid | Status bits—external latches 1: Valid; 0: invalid | 0.1 | BIT | 0.1 |
| 60n0:03 | Status_Set counter done | Status Bit - Set the count value complete 1: Valid; 0: invalid | 0.2 | BIT | 0.1 |
| 60n0:04 | Status_TxPDO State | TxPDO Status bit | 0.3 | BIT | 0.1 |
| 60n0:05 | Status_Direction inversion detected | Status bits-Reverse monitoring of direction 1: Reverse; 0: Forward | 0.4 | BIT | 0.1 |
| 60n0:06 | Status_Counter value out of range | Status bits -Overflow of value 1: Overflow; 0: has not overflowed | 0.5 | BIT | 0.1 |
| --- | --- | Undefined | 0.6 |  | 1.2 |
| 60n0:08 | Counter value | Encoder count value | 2.0 | DINT | 4.0 |
| 60n0:09 | Latch value | External latch count value | 6.0 | DINT | 4.0 |
| 60n0:0A | Latch Z value | Z-phase latch count value | 10.0 | DINT | 4.0 |

Process data object contents PDO Content(0x160n)

| Index(hex) | Name | Description | Offset (Byte) | Data type | Size (Byte) |
| --- | --- | --- | --- | --- | --- |
| 70n0:01 | Control_Enable latch Z | Z-phase latching is enabled 1: Enabled 0: Not enabled | 0.0 | BIT | 0.1 |
| 70n0:02 | Control_Enable latch extern on positive edge | Enables latch external on positive edge 1: Enabled 0: Not enabled | 0.1 | BIT | 0.1 |
| 70n0:03 | Control_Set counter | Set the count value | 0.2 | BIT | 0.1 |
| 70n0:04 | Control_Enable latch extern on negative edge | Enable latch external on negative edge 1: Enabled 0: Not enabled | 0.3 | BIT | 0.1 |
| 70n0:05 | Control_Set counter on latch Z | Set the count value at the Z-phase latching moment | 0.4 | BIT | 0.1 |
| --- | --- | Undefined | 0.5 |  | 1.3 |
| 70n0:07 | Set counter value | Set the count value | 2.0 | DINT | 4.0 |

SDO Service Data

0x80n0*** encoder input settings (2 channels: 0≤n≤1)

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| 80n0:0 | Encoder Settings Ch.n+1 | Channel n+1 encoder settings |  |  | 06 |
| 80n0:01 | Enable Z reset | Enable Z signal reset count value | BOOLEAN | RW | 0B |
| 80n0:02 | Enable extern reset | Enable the external signal to reset the count value | BOOLEAN | RW | 0B |
| 80n0:03 | Enable direction inversion | Enables the encoder to count in the opposite direction 0: Positive; 1: Reverse | BOOLEAN | RW | 0B |
| 80n0:04 | Evaluation mode | Encoder counting multiplier mode selection 0: 4 ×; 1:2 × | BOOLEAN | RW | 0B |
| 80n0:05 | ENC filter settings | Encoder count filter settings 0~15, default 8 | BIT4 | RW | 08 |
| 80n0:06 | Latch extern filter settings | External latch filter settings 0~15, default 8 | BIT4 | RW | 08 |

0xF008*** Parameter Handling

| Index(hex) | Name | Description | Data type | Flag bit | Default value(hex) |
| --- | --- | --- | --- | --- | --- |
| F008:0 | Parameter Handling | Parameter handling | INT8 | RO | 04 |
| F008:01 | Save Current Parameters | Save the current set parameters, enter 0x1234 to save the parameters, and the value is 0 after saving is completed. | UINT16 | RW | 0000 |
| F008:02 | Restore Default Parameters | Restore ex-factory parameters, enter 0 x 1234 to restore default parameters, and the value is 0 after the restoration is completed. | UINT16 | RW | 0000 |
| F008:03 | Checksum | Parameter checksums | UINT16 | RO | _ |
| F008:04 | Manufacturer Reserve | Vendor reserved | UINT16 | RW | 0000 |

Special Features

Data Calibration

The AI analog input and AO analog output modules of SC series module are factory calibrated (Vendor Calibration), and the input and output analog quantities of AI and AO ports are very close to the actual value. Of course, the user can select User Calibration for more accurate measurements and outputs.

The data processing process is as follows:

MC3xxx calibration process

ADC acquisition value X

Enable Vendor Calibration? (0x80+n0:02=1)

Enable User Calibration? (0x80 n0:01=1)

The slave accepts the value X

The master accepts the value X

MC4xxx calibration process

Enable Vendor Calibration? (0x80+n0:02=1)

Output X to DAC

Enable User Calibration? (0x80 n0:01=1)

FAQ