Manual of

SRR Series Plug-in I/O Products(PROFINET Coupler)

SINSEGYE (Shenzhen) Computer System Co., Ltd.

V1.0

Contents

1 Product Overview	1

1.1 Product introduction	1

1.2 Product features	1

1.3 Application mode	1

2 List of Modules	3

2.1 List of Modules	3

3 Introduction of Modules	4

3.1 PROFINET coupler	4

3.1.1 Panel structure	4

3.1.2 Indicator functions	4

3.1.3 Technical specifications	6

3.1.3.1 Port parameters	6

3.1.3.2 Power parameters	6

3.1.3.3 General parameters	6

3.1.4 Power wiring diagram	8

3.1.5 Fieldbus wiring	8

3.1.6 Overall dimension drawing	9

3.2 Digital I/O terminal	10

3.2.1 Indicator functions	10

3.2.2 Technical specifications	10

3.2.2.1 Digital input module parameters	10

3.2.2.2 Digital output module parameters	10

3.2.2.1 General technical parameters	11

3.2.2.2 Wiring diagram	12

3.2.2.3 SRR1016	12

3.2.2.4 SRR2116	13

3.2.2.5 SRR2216	14

3.2.3 Outline dimension drawing	15

3.3 Analog I/O terminal	16

3.3.1 Indicator functions	16

3.3.2 Technical specifications	16

3.3.2.1 Analog input module parameters	16

3.3.2.2 Analog output module parameters	17

3.3.2.3 General technical parameters	18

3.3.3 Analog voltage parameters	18

3.3.3.1 Voltage input range selection table	18

3.3.3.2 Voltage output range selection table	18

3.3.3.3 Voltage input code value table	18

3.3.3.4 Voltage output code value table	21

3.3.4 Analog current parameters	23

3.3.4.1 Current input range selection table	23

3.3.4.2 Voltage output range selection table	23

3.3.4.3 Current input code value table	23

3.3.4.4 Current output code value table	24

3.3.5 Wiring diagram	24

3.3.5.1 SRR3214	24

3.3.5.2 SRR3234	26

3.3.5.3 SRR4014	27

3.3.5.4 SRR4034	28

3.3.6 Overall dimension drawing	29

3.4 Terminal cover	30

3.4.1 Overall dimension drawing	30

4 Installation and Removal	31

4.1 Installation guide	31

4.2 Installation and removal steps	32

4.3 Installation/removal schematic diagram	33

5 Wiring	38

5.1 Wiring terminal	38

5.2 Wiring instructions and requirements	38

6 Usages	40

6.1 Description of parameters	40

6.1.1 Digital input filtering	40

6.1.2 Digital output signal clearing/holding	41

6.1.3 Digital input value when the module fails	41

6.1.4 Analog range setting	41

6.1.5 Analog input filtering	41

6.1.6 Analog output signal clearing/holding	42

6.1.7 Analog value power-off preservation	42

6.1.8 Coupler parameters	43

6.1.8.1 Alarm function settings	43

6.1.8.2 PLC stop status output control	43

6.2 Alarm Function	44

6.2.1 General fault codes of coupler	44

6.2.2 Viewing fault codes	44

6.3 MRP ring network redundancy	46

6.4 Hardware detection	46

6.5 Configuration application of PROFINET coupler	47

6.5.1 Application in TIA Portal V17 software environment	47

6.5.2 Ring network redundancy configuration application	68

Product Overview

Product introduction

The SRR series plug-in I/O terminal is a combination structure of couplers and I/O terminals. The coupler is used to connect the extensible I/O terminal to the real-time industrial Ethernet system, and the S-Link fieldbus is used on the backplane. The coupler module is used for the communication of the fieldbus, to realize the real-time data exchange function between various I/O terminals and the couplers/controllers.

The SRR series plug-in I/O terminal has rich varieties and high real-time performance, which can provide the supports for users to collect data at high speed, optimize system configuration, simplify field wiring and improve system reliability.

Product features

- Less occupied nodes

A node consists of a fieldbus coupler, 1~32 SRR series I/O terminals and a terminal cover.

- Rich functional expansion

It supports flexible expansion and complete I/O terminal types, and can integrate various digital modules and analog modules to meet the needs of different applications.

- Flexible configuration

Various types of plug-in I/O terminals can be combined flexibly.

- Strong compatibility

The communication ports of couplers meet the communication standard and support the mainstream EtherCAT master station.

- Small volume

It has compact structure and small occupied space.

- Easy diagnosis

The indicators are complete, the module status is clear and the test and maintenance are convenient.

- High speed

The S-Link fieldbus is used on the backplane, with the minimum scanning cycle of 200 us, and the typical value of 1 ms.

- Easy installation

It is installed with DIN 35 mm standard guide rail.

The elastic terminal is used, to ensure convenient and quick wiring.

Application mode

| The coupler module is connected with the controller in the application site, and the I/O terminal is used to connect the input and output sensors in the application site. Usually, the process of data acquisition and processing control is as follows: A.The input I/O terminals collect various signals on site and sent them the coupler via the internal fieldbus; B.The controller reads the data from the coupler via the fieldbus or industrial Ethernet, processes the data, and then writes the output data into the coupler; - C.The coupler writes the output data to the output I/O terminals via the internal fieldbus, to control the device. The extensible I/O terminals include digital input module, digital output module, analog input module and analog output module. Application mode: Use the combination application mode of coupler, digital, analog and other modules. Application configuration: It can adapt to the combination configuration of different models of I/O terminals according to the requirements of master station access capacity, number of stations, I/O points, and function types. Configuration rules: Coupler module, I/O terminals, terminal cover are configured from left to right. The combination application mode of coupler, I/O terminals and terminal cover is used in the product, including the following combinations. Combination mode I (coupler module, I/O terminals and terminal cover) |  |
| --- | --- |

List of Modules

List of Modules

| Model | Product description |  |
| --- | --- | --- |
| SRR8300 | PROFINET fieldbus coupler module |  |
| SRR1016 | 16-channel digital input module, input NPN/PNP compatible, input filtering time of 3 ms by default |  |
| SRR2116 | 16-channel digital output module, output NPN type |  |
| SRR2216 | 16-channel digital output module, output PNP type |  |
| SRR3214 | 4-channel analog voltage input module | Single-port signal with adjustable range: Disable, -10V~+10V, 0V~10V, -5V~+5V, 0V~5V and 1V~5V |
| SRR3234 | 4-channel analog current input module | Single-port signal with adjustable range: Disable, 4mA~20mA and 0mA~20mA |
| SRR4014 | 4-channel analog voltage output module | Single-port signal with adjustable range: Disable, -10V~+10V, 0V~10V, -5V~+5V, 0V~5V and 1V~5V |
| SRR4034 | 4-channel analog current output module | Single-port signal with adjustable range: Disable, 4mA~20mA and 0mA~20mA |
| SRR9010 | Terminal cover |  |

Introduction of Modules

PROFINET coupler

Panel structure

| No. | Name | Description |
| --- | --- | --- |
| ① | Module indicator and indicator ID | Indicate the coupler power state and the system operation state |
| ② | Power terminal | 6P snap-in wiring terminal |
| ③ | Fieldbus portX1 | RJ45 port |
| ④ | Fieldbus portX2 | RJ45 port |
| ⑤ | Guide rail slot | Fix DIN 35 mm guide rail |

Indicator functions

| Definition of PROFINET coupler indicators |  |  |  |  |
| --- | --- | --- | --- | --- |
| ID | Name | Color | Status | Description |
| PWR | Power indicator | Green | ON | The module power supply is running normally |
|  |  |  | OFF | The power supply is not running or abnormal |
| OVR | Overload indicator | Red | OFF | No overloaded |
|  |  |  | ON | At more than 90% (±5%) of the load |
| RUN | running status indicator | Green | ON | The system is running normally |
|  |  |  | OFF | Abnormal work |
| BF | Bus Exception Indicator | Red | Flashing | PROFINET bus parameters are not set or are abnormal. |
|  |  |  | OFF | PROFINET bus parameters are normal |
| IOR | IO communication indicator | Green | ON | I/O process data has been established |
|  |  |  | Flash at1Hz | No business data interaction |
|  |  |  | Flash at10Hz | Firmware upgrade of coupler |
| IOE | IO abnormal indicator | Red | ON | Communication abnormality |
|  |  |  | Flash at1Hz | I/O terminal abnormality alarm |
|  |  |  | OFF | No communication abnormality |

| Definition of network status indicators |  |  |  |  |
| --- | --- | --- | --- | --- |
| ID | Name | Color | Status | Description |
| X1 | Network status indicato | Orange | Flash | The connection is established and there is data interaction |
|  |  |  | OFF | There is no data interaction or there is an abnormality |
|  |  | Green | ON | The network connection is established |
|  |  |  | OFF | The network connection is not established or abnormal. |
| X2 | Network status indicato | Orange | Flash | The connection is established and there is data interaction |
|  |  |  | OFF | There is no data interaction or there is an abnormality |
|  |  | Green | ON | The network connection is established |
|  |  |  | OFF | The network connection is not established or abnormal. |

Technical specifications

Port parameters

| PROFINET port parameters |  |
| --- | --- |
| Fieldbus protocol | PROFINET |
| Number of slave stations | Depends on the number of slave stations supported by the master station |
| Data transmission medium | EtherCAT CAT5 cable |
| Transmission rate | 100Mbps |
| Minimum cycle time [1] | 1ms |
| Transmission distance | ≤100m(station-station distance) |
| Fieldbus port | 2×RJ45 |
| Maximum serial number of modules | 32 |
| Input and output process data volume | 1024Bytes[2] |

Note [1]: It refers to the cycle time between PLC and coupler (scanning cycle).

Note [2]: The total length of uplink and downlink data does not exceed 1024Bytes.

Power parameters

| Power parameters |  |
| --- | --- |
| Input voltage | SELV Input 24VDC（18V~36V） |
| Input current | Max：600mA（24VDC） |
| Backplane power current | Max：2A |
| Backplane power voltage | 5VDC |

General parameters

| General technical parameters |  |  |
| --- | --- | --- |
| Dimensions |  | 100◊27.82◊80 mm |
| Mass |  | 105g |
| Operating environment | Operating temperature | -20℃~+60℃ |
|  | Storage temperature | -40℃~+80℃ |
|  | Relative humidity | 95%，no condensation |
|  | Altitude | ≤2000m |
|  | Protection grade | IP20 |
|  | Overvoltage category | I |
|  | Pollution level | Level 2 |

| PROFINET IO RT | Support |
| --- | --- |
| abnormal self-recovery | Support |
| Hardware detection function | Support |
| Diagnosis | Support |
| Alarm | Support |
| Firmware upgrade | Support |
| Short circuit protection | Support |
| Reverse connection protection | support (automatic recovery mechanism) |
| Surge protection | support (automatic recovery mechanism) |
| Diagnosis | Support |

Power wiring diagram

Use the 24VDC power module, connect the power supply with the wiring method as shown below, and a reliably ground the PE (twisted pair is recommended for the power cable).

*24V internal conduction, 0V internal conduction.

Fieldbus wiring

Use standard RJ45 network port and standard crystal connector; the pin distribution is shown in the following table.

| Pin No. | Signal |
| --- | --- |
| 1 | TD+ |
| 2 | TD- |
| 3 | RD+ |
| 4 | 一 |
| 5 | 一 |
| 6 | RD- |
| 7 | 一 |
| 8 | 一 |

Notes

- It is recommended to use Category 5 or higher double shielded (woven net + aluminum foil) STP cable as communication cable.

- The length of cables between devices cannot exceed 100 m.

Overall dimension drawing

Dimensions of coupler (mm)

Digital I/O terminal

Indicator functions

| Definition of digital I/O terminal indicators |  |  |  |  |
| --- | --- | --- | --- | --- |
| ID | Name | Color | Status | Description |
| PWR | Power indicator | Green | ON | The power supply is normal |
|  |  |  | OFF | The product is not powered on or the power supply is abnormal |
| RUN | Running status indicator | Green | ON | The system is running normally |
|  |  |  | Flash at 1Hz | There is no business data interaction, which shall be established |
|  |  |  | Flash at 10Hz | Firmware upgrade |
|  |  |  | OFF | The system is not running |
| 0~7 | Input channel indicator | Green | ON | There is signal input in the module channel |
|  |  |  | OFF | There is no signal input or abnormal signal input in the module channel |
| 0~7 | Output channel indicator | Green | ON | There is signal input in the module channel |
|  |  |  | OFF | There is no signal input or abnormal signal input in the module channel |

Technical specifications

Digital input module parameters

| Digital input |  |
| --- | --- |
| Product model | SRR1016 |
| Rated voltage of fieldbus input power | 5VDC (4.5V ~ 5.5V) |
| Rated current of fieldbus input power | ≤50mA |
| Rated input voltage | 24 VDC (20.4 V ~ 28.8 V) |
| Typical input current | 5mA/ch (24 VDC) |
| Input signal points | 16 |
| Input signal type | NPN/PNP compatible |
| Input signal form | Voltage direct input forms Sink: NPN open collector input Source: PNP open collector input |
| OFF voltage /OFF current | Below -3V ~ +5V/0.9mA |
| ON voltage/ON current | Above 11V~30V/2.1mA |
| Response time | <50us |
| Input filtering | No filtering, 0.1ms, 0.2ms, 0.5ms, 1ms, 2ms, 3ms (factory setting), 4ms...18ms, 19ms, 20ms |
| Maximum input frequency | 150Hz (filtering time: 3ms) |
| Input impedance | 5.4KΩ |
| Isolation mode | Optocoupler isolation |
| Isolation withstand voltage | 500VAC |
| Rated current loss | 50mA |
| Power consumption | 0.25W |
| Digital input type | Type1/Type3 |
| Channel indicator | Green LED |

Digital output module parameters

| Digital output |  |  |
| --- | --- | --- |
| Product model | SRR2116 | SRR2216 |
| Rated voltage of fieldbus input power | 5VDC (4.5V ~ 5.5V) |  |
| Rated current of fieldbus input power | ≤75mA | ≤55mA |
| Input voltage range on the field side | 24 VDC (20.4 V ~ 28.8 V) |  |
| Output signal points | 16 | 16 |
| Output signal types | NPN | PNP |
| Output voltage drop | ＜1V |  |
| Output load types | Resistive load, inductive load and indicator load |  |
| Single-channel rated current | Max: 0.5A |  |
| Leakage current | <10uA |  |
| Response time | <150us |  |
| Output channel protection | Short circuit protection (automatic recovery mechanism) |  |
| Module protection | Reverse connection protection (automatic recovery mechanism), surge protection on the field side |  |
| Isolation mode | Optocoupler isolation |  |
| Isolation withstand voltage | 500VAC |  |
| Rated current loss | 75mA | 55mA |
| Power consumption | 0.375W | 0.275W |
| Channel indicator | Green LED |  |

      - General technical parameters

| General technical parameters |  |
| --- | --- |
| Dimensions | 100x16.11x80mm |
| Mass | 70g |
| Operating temperature | -20℃~+60℃ |
| Storage temperature | -40℃~+80℃ |
| Relative humidity | 95%, no condensation |
| Altitude | ≤2000m |
| Pollution level | Level 2 |
| Protection grade | IP20 |

Wiring diagram

SRR1016

*COM internal conduction; NPN/PNP compatible

SRR2116

SRR2216

Outline dimension drawing

16 channels Dimensions of digital I/O terminal (mm)

Analog I/O terminal

Indicator functions

| Definition of analog I/O terminal indicators |  |  |  |  |
| --- | --- | --- | --- | --- |
| ID | Name | Color | Status | Description |
| PWR | Power indicator | Green | ON | The power supply is normal |
|  |  |  | OFF | The product is not powered on or the power supply is abnormal |
| RUN | Running status indicator | Green | ON | The system is running normally |
|  |  |  | Flash at 1Hz | There is no business data interaction, which shall be established |
|  |  |  | Flash at 10Hz | Firmware upgrade |
|  |  |  | OFF | The system is not running |
| 0~7 | Input channel indicator | Green | ON | There is signal input in the module channel |
|  |  |  | OFF | There is no signal input or abnormal signal input in the module channel |
| 0~7 | Output channel indicator | Green | ON | There is signal input in the module channel |
|  |  |  | OFF | There is no signal input or abnormal signal input in the module channel |

Technical specifications

Analog input module parameters

| Analog input |  |  |
| --- | --- | --- |
| Product model | SRR3214 | SRR3234 |
| Rated voltage of fieldbus input power | 5VDC (4.5V ~ 5.5V) |  |
| Rated current of fieldbus input power | ≤145mA | ≤70mA |
| Input points | 4 | 4 |
| Input types | Voltage type | Current type |
| Input signals | Disable,-10V to+-10V~+10V to 10V, -5V~+5V, 0V~5V, 1V~5V (adjustable range, -10V~+10V by default) | Disable, 4mA~20mA and 0mA~20mA (adjustable range, 0mA~20mA by default) |
| Input signal type | Single-port signal |  |
| Channel response time | 230us/ch 380us/4ch | 230us/ch 300us/4ch |
| Resolution | 16bits |  |
| Sampling rate (all channels) | ≤1ksps |  |
| Accuracy | ±0.3%0.1% at 25℃; 0.3% within the whole temperature range |  |
| Input filtering | Support |  |
| Smoothing series | 1~200 |  |
| Input impedance (voltage type) | ≥400kΩ | - |
| Input impedance (current type) | - | ≤100Ω |
| Maximum allowable voltage of channel (voltage type) | 30V | - |
| Maximum allowable channel current (current type) | - | 30mA |
| No affect on the system | When the ±15V power supply is damaged and short-circuited, the system +5V power shall not be affected |  |
| Potential isolation | There is no isolation between channels, and there is isolation between channel and backplane fieldbus, and between channels and power voltage |  |
| Input overload protection | Support clamping protection | Support current limiting protection |
| Input protection | ±30V | ±30mA |
| Isolation withstand voltage | 500VDC |  |
| Rated current loss | 145mA | 70mA |
| Power consumption | 0.725W | 0.35W |
| Channel indicator | Green LED |  |

Analog output module parameters

| Analog output |  |  |
| --- | --- | --- |
| Product model | SRR4014 | SRR4034 |
| Rated voltage of fieldbus input power | 5VDC (4.5V ~ 5.5V) |  |
| Rated current of fieldbus input power | ≤30mA |  |
| Input voltage range on the field side | 24 VDC (20.4 V ~ 28.8 V) |  |
| Output points | 4 | 4 |
| Output types | Voltage type | Current type |
| Output signals | Disable,-10V to+-10V~+10V to 10V, -5V~+5V, 0V~5V and 1V~5V (adjustable range, -10V~+10V by default) | Disable, 4mA~20mA and 0mA~20mA (adjustable range, 0mA~20mA by default) |
| Channel response time | 200us/ch 200us/4ch |  |
| Resolution | 16bits |  |
| Accuracy | 0.1% at 25℃; 0.3% within the whole temperature range |  |
| Load impedance (voltage type) | ≥ 2kΩ (1kΩ accuracy: 3 % at 25℃; 5 ‰ with the whole temperature range) | - |
| Load impedance (current type) | - | ≤500Ω |
| No affect on the system | When the ±15V power supply is damaged and short-circuited, the system +5V power supply shall not be affected |  |
| Output protection | Overload protection, open circuit protection and short circuit protection (with automatic recovery mechanisms) |  |
| Potential isolation | There is no isolation between channels, and there is isolation between channel and backplane fieldbus, and between channel and power voltage |  |
| Isolation withstand voltage | 500VDC |  |
| Rated current loss | 30mA |  |
| Power consumption | 0.15W |  |
| Optional clearing/holding functions in non-OP state | Support |  |
| Channel indicator | Green LED |  |

General technical parameters

| General technical parameters |  |
| --- | --- |
| Dimensions | 100 x16.11 x 80mm |
| Mass | 70g |
| Operating temperature | -20℃~+60℃ |
| Storage temperature | -40℃~+80℃ |
| Relative humidity | 95%, no condensation |
| Altitude | ≤2000m |
| Pollution level | Level 2 |
| Protection grade | IP20 |

Analog voltage parameters

Voltage input range selection table

| Voltage input range selection and code value range |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Range selection | Measuring range | Code value range | Voltage input calculation formula | Voltage output calculation formula | Code value correspondence table |
| 0 | Disable, indicating that the channel is not enabled |  |  |  |  |
| 1 | -10V~+10V | -32768~32767 | D=(65535/20)*U | U=(D*20)/65535 | See Section 3.3.4.3 “Voltage input code value table” |
| 2 | 0V~10V | 0~32767 | D=(32767/10)*U | U=(D*10)/32767 |  |
| 3 | -10V~+10V | -27648~27648 | D=(55296/20)*U | U=(D*20)/55296 |  |
| 4(by default) | 0V~10V | 0~27648 | D=(27648/10)*U | U=(D*10)/27648 |  |
| 5 | -5V~+5V | -27648~27648 | D=(55296/10)*U | U=(D*10)/55296 |  |
| 6 | 0V~5V | 0~27648 | D=(27648/5)*U | U=(D*5)/27648 |  |
| 7 | 1V~5V | 0~27648 | D=(27648/4)*U-6912 | U=(D+6912)*4/27648 |  |

Note: D represents code value, U represents voltage, and the default range of analog voltage input module is 4:0V ~10V (0~ 27648).

Voltage output range selection table

| Voltage output range selection and code value range |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Range selection | Measuring range | Code value range | Voltage input calculation formula | Voltage output calculation formula | Code value correspondence table |
| 0 | Disable, indicating that the channel is not enabled |  |  |  |  |
| 1 | -10V~+10V | -32768~32767 | D=(65535/20)*U | U=(D*20)/65535 | See Section 3.3.4.4 “Voltage output code value table” |
| 2 | 0V~10V | 0~32767 | D=(32767/10)*U | U=(D*10)/32767 |  |
| 3 | -10V~+10V | -27648~27648 | D=(55296/20)*U | U=(D*20)/55296 |  |
| 4(by default) | 0V~10V | 0~27648 | D=(27648/10)*U | U=(D*10)/27648 |  |
| 5 | -5V~+5V | -27648~27648 | D=(55296/10)*U | U=(D*10)/55296 |  |
| 6 | 0V~5V | 0~27648 | D=(27648/5)*U | U=(D*5)/27648 |  |
| 7 | 1V~5V | 0~27648 | D=(27648/4)*U-6912 | U=(D+6912)*4/27648 |  |

Note: D represents code value, U represents voltage, and the default range of analog voltage output module is 4: 0V ~10V (0~27648).

Voltage input code value table

| Measuring range Voltage | -10V~+10V | 0V~10V | -10V~+10V | 0V~10V |
| --- | --- | --- | --- | --- |
|  | -32768~32767 | 0~32767 | -27648~27648 | 0~27648 |
|  | Code value | Code value | Code value | Code value |
| -10.13 | - | - | -27980 | - |
| -10 | -32768 | - | -27648 | - |
| -9 | -29491 | - | -24883 | - |
| -8 | -26214 | - | -22118 | - |
| -7 | -22937 | - | -19354 | - |
| -6 | -19661 | - | -16589 | - |
| -5 | -16384 | - | -13824 | - |
| -4 | -13107 | - | -11059 | - |
| -3 | -9830 | - | -8294 | - |
| -2 | -6554 | - | -5530 | - |
| -1 | -3277 | - | -2765 | - |
| -0.13 | -426 | -384 | -359 | -332 |
| -0.06 | -197 | -197 | -166 | -156 |
| 0 | 0 | 0 | 0 | 0 |
| 1 | 3277 | 3277 | 2765 | 2765 |
| 2 | 6554 | 6554 | 5530 | 5530 |
| 3 | 9830 | 9830 | 8294 | 8294 |
| 4 | 13107 | 13107 | 11059 | 11059 |
| 5 | 16384 | 16384 | 13824 | 13824 |
| 6 | 19661 | 19661 | 16589 | 16589 |
| 7 | 22937 | 22937 | 19354 | 19354 |
| 8 | 26214 | 26214 | 22118 | 22118 |
| 9 | 29491 | 29491 | 24883 | 24883 |
| 10 | 32767 | 32767 | 27648 | 27648 |
| 10.12 | - | - | 27980 | 27980 |
| Code value formula | Code value =(65535/20)*Voltage | Code value =(32767/10)*Voltage | Code value =(55296/20)*Voltage | Code value =(27648/10)*Voltage |
| Voltage formula | Voltage = (Code value*20)/65535 | Voltage = (Code value*10)/32767 | Voltage = (Code value*20)/55296 | Voltage = (Code value*10)/27648 |

Notes: ① When the measuring range of voltage input module is -10V~+10V(-32768~32767), it will support the upper and lower overflow function, that is, when the channel input voltage is more than 10V, the maximum code value of 32767 will be displayed; when the channel input voltage is less than -10V, the minimum code value of -32768 will be displayed.

② When the measuring range of the voltage input module is 0V~10V(0~32767), it will support the functions of lower overflow overshoot, upper and lower overflow and lower overflow alarm. The overshoot means that the channel input range will enter the overshoot when it exceeds the measuring range, and the normal calculation code value will be displayed within the range of -0.13V~+10V. The upper and lower overflow means that when the maximum code value of 32767 will be displayed when the channel input voltage is more than 10V; when the channel input voltage is less than -0.13V, the minimum overshoot code value of -384 will be displayed and an alarm will be given.

③ When the measuring range of voltage input module is -10V~+10V (-27648 ~ 27648), it will support the functions of overshoot, upper and lower overflow and upper and lower overflow alarm. The overshoot means that the channel input range will enter the overshoot when it exceeds the range, and the normal calculation code value will be displayed within the range of -10.13 V ~+10.12 V. The upper and lower overflow means that when the channel input voltage is more than 10.12V, the maximum overshoot code value of 27980 will be displayed and an alarm will be given; when the channel input voltage is less than -10.13V, the minimum overshoot code value of -27980 will be displayed and an alarm will be given.

④ When the range of voltage input module is 0V~10V(0~27648), it will support the functions of overshoot, upper and lower overflow and upper and lower overflow alarm. The overshoot means that the channel input range will enter the overshoot when it exceeds the ranged, and the normal calculation code value will be displayed within the range of -0.13 V ~+10.12 V. The upper and lower overflow means that when the channel input voltage is more than 10.12V, the maximum overshoot code value of 27980 will be displayed and an alarm will be given; when the channel input voltage is less than -0.13V, the minimum overshoot code value of -332 will be displayed and an alarm will be given.

| Measuring range Voltage | -5V~+5V | 0V~5V | 1V~5V |
| --- | --- | --- | --- |
|  | -27648~27648 | 0~27648 | 0~27648 |
|  | Code value | Code value | Code value |
| -5.07 | -27980 | - | - |
| -5 | -27648 | - | - |
| -4 | -22118 | - | - |
| -3 | -16588 | - | - |
| -2 | -11060 | - | - |
| -1 | -5530 | - | - |
| -0.07 | -332 | -332 | - |
| 0 | 0 | 0 | - |
| 0.94 | 5198 | 5198 | -345 |
| 1 | 5530 | 5530 | 0 |
| 2 | 11060 | 11060 | 6912 |
| 3 | 16588 | 16588 | 13824 |
| 4 | 22118 | 22118 | 20736 |
| 5 | 27648 | 27648 | 27648 |
| 5.06 | 27980 | 27980 | 27933 |
| Code value formula | Code value =(55296/10)* Voltage | Code value =(27648/5)*Voltage | Code value =(27648/4)*Voltage -6912 |
| Voltage formula | Voltage = (Code value*10)/55296 | Voltage = (Code value*5)/27648 | Voltage = (Code value +6912)*4/27648 |

Notes: ① When the measuring range of voltage input module is -5V~+5V(-27648~27648), it will support the functions of overshoot, upper and lower overflow and upper and lower overflow alarm. The overshoot means that the channel input voltage will enter the overshoot when it exceeds the range, and the normal calculation code value will be displayed within the range of -5.07V ~+5.06V. The upper and lower overflow means that when the channel input voltage is more than 5.06V, the maximum overshoot code value of 27980 will be displayed and an alarm will be given; when the channel input voltage is less than -5.07V, the minimum overshoot code value of -27980 will be displayed and an alarm will be given.

② When the measuring range of voltage input module is 0V~5V(0~27648), it will support the functions of overshoot, upper and lower overflow and upper and lower overflow alarm. The overshoot means that the channel input range will enter the overshoot when it exceed the range, and the normal calculation code value will be displayed within the range of -0.07 V ~+5.06 V. The overflow means that when the channel input voltage is more than 5.06V, the maximum overshoot code value of 27980 will be displayed and an alarm is given; when the channel input voltage is less than -0.07V, the minimum overshoot code value of -332 will be displayed and an alarm will be given.

③ When the measuring range of voltage input module is 1V~5V(0~27648), it will support the functions of overshoot, upper and lower overflow and upper and lower overflow alarm. The overshoot means that the channel input voltage will enter the overshoot when it exceeds the range, and the normal calculation code value will be displayed within the range of 0.94 V ~ 5.06 V. The overflow means that when the channel input voltage is more than 5.06V, the maximum overshoot code value of 27933 will be displayed and an alarm will be given; when the channel input voltage is less than 0.94V, the minimum overshoot code value of -345 will be displayed and an alarm will be given.

Voltage output code value table

| Measuring range Voltage | -10V~+10V | 0V~10V | -10V~+10V | 0V~10V |
| --- | --- | --- | --- | --- |
|  | -32768~32767 | 0~32767 | -27648~27648 | 0~27648 |
|  | Code value | Code value | Code value | Code value |
| -10 | -32768 | - | -27648 | - |
| -9 | -29491 | - | -24883 | - |
| -8 | -26214 | - | -22118 | - |
| -7 | -22937 | - | -19354 | - |
| -6 | -19661 | - | -16589 | - |
| -5 | -16384 | - | -13824 | - |
| -4 | -13107 | - | -11059 | - |
| -3 | -9830 | - | -8294 | - |
| -2 | -6554 | - | -5530 | - |
| -1 | -3277 | - | -2765 | - |
| 0 | 0 | 0 | 0 | 0 |
| 1 | 3277 | 3277 | 2765 | 2765 |
| 2 | 6554 | 6554 | 5530 | 5530 |
| 3 | 9830 | 9830 | 8294 | 8294 |
| 4 | 13107 | 13107 | 11059 | 11059 |
| 5 | 16384 | 16384 | 13824 | 13824 |
| 6 | 19661 | 19661 | 16589 | 16589 |
| 7 | 22937 | 22937 | 19354 | 19354 |
| 8 | 26214 | 26214 | 22118 | 22118 |
| 9 | 29491 | 29491 | 24883 | 24883 |
| 10 | 32767 | 32767 | 27648 | 27648 |
| Code value formula | Code value =(65535/20)*Voltage | Code value =(32767/10)*Voltage | Code value =(55296/20)*Voltage | Code value =(27648/10)*Voltage |
| Voltage formula | Voltage = (Code value*20)/65535 | Voltage = (Code value*10)/32767 | Voltage = (Code value*20)/55296 | Voltage = (Code value*10)/27648 |

Notes: ① The voltage output module supports upper and lower overflow function, that is, when the measuring range of the voltage output module is -10V~+10V or 0V~10V, and the code value is set to be more than the maximum code value corresponding to the range, all channels will output the voltage of 10V;

When the measuring range of the voltage output module is -10V to+10V and the code value is set to be less than the minimum code value corresponding to the range, all channels will output the voltage of -10V;

When the measuring range of the voltage output module is 0V~10V and the code value is set to be less than the minimum code value corresponding to the range, all channels will output the voltage of 0V.

| Measuring range Voltage | -5V~+5V | 0V~5V | 1V~5V |
| --- | --- | --- | --- |
|  | -27648~27648 | 0~27648 | 0~27648 |
|  | Code value | Code value | Code value |
| -5 | -27648 | - | - |
| -4 | -22118 | - | - |
| -3 | -16588 | - | - |
| -2 | -11060 | - | - |
| -1 | -5530 | - | - |
| 0 | 0 | 0 | - |
| 1 | 5530 | 5530 | 0 |
| 2 | 11060 | 11060 | 6912 |
| 3 | 16588 | 16588 | 13824 |
| 4 | 22118 | 22118 | 20736 |
| 5 | 27648 | 27648 | 27648 |
| Code value formula | Code value =(55296/10)*Voltage | Code value =(27648/5)*Voltage | Code value =(27648/4)*Voltage -6912 |
| Voltage formula | Voltage = (Code value*10)/55296 | Voltage = (Code value*5)/27648 | Voltage = (Code value +6912)*4/27648 |

Notes: ① The voltage output module supports the upper and lower overflow function, that is, when the measuring range of the voltage output module is -5V~+5V/0V~5V/1V~5V and the code value is set to be more than the maximum code value corresponding to the range, all channels will output the voltage of 5V;

When the measuring range of the voltage output module is -5V~+5V and the code value is set to be less than the minimum code value corresponding to the range, all channels will output the voltage of -5V;

When the measuring range of the voltage output module is 0V~5V and the code value is set to be less than the minimum code value corresponding to the range, all channels will output the voltage of 0V;

When the measuring range of voltage output module is 1V~5V and the code value is set to be less than the minimum code value corresponding to the range, all channels will output the voltage of 1V.

    - Analog current parameters

Current input range selection table

| Voltage input range selection and code value range |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Range selection | Measuring range | Code value range | Voltage input calculation formula | Voltage output calculation formula | Code value correspondence table |
| 0 | Disable, indicating that the channel is not enabled |  |  |  |  |
| 1 | -10V~+10V | -32768~32767 | D=(65535/20)*U | U=(D*20)/65535 | See Section 3.3.5.3 “Voltage input code value table” |
| 2 | 0V~10V | 0~32767 | D=(32767/10)*U | U=(D*10)/32767 |  |
| 3(by default) | -10V~+10V | -27648~27648 | D=(55296/20)*U | U=(D*20)/55296 |  |
| 4 | 0V~10V | 0~27648 | D=(27648/10)*U | U=(D*10)/27648 |  |

Note: D represents code value, U represents voltage, and the default range of analog voltage input module is 3：4mA~20mA（0~27648）.

Voltage output range selection table

| Voltage output range selection and code value range |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Range selection | Measuring range | Code value range | Voltage input calculation formula | Voltage output calculation formula | Code value correspondence table |
| 0 | Disable, indicating that the channel is not enabled |  |  |  |  |
| 1 | -10V~+10V | -32768~32767 | D=(65535/20)*U | U=(D*20)/65535 | See Section 3.3.5.4 “Voltage output code value table” |
| 2 | 0V~10V | 0~32767 | D=(32767/10)*U | U=(D*10)/32767 |  |
| 3(by default) | -10V~+10V | -27648~27648 | D=(55296/20)*U | U=(D*20)/55296 |  |
| 4 | 0V~10V | 0~27648 | D=(27648/10)*U | U=(D*10)/27648 |  |

Note: D represents code value, U represents voltage, and the default range of analog voltage output module is 3：4mA~20mA（0~27648）.

Current input code value table

| Measuring range Current | 4mA~20mA | 0mA~20mA | 4mA~20mA | 0mA~20mA |
| --- | --- | --- | --- | --- |
|  | 0~65535 | 0~65535 | 0~27648 | 0~27648 |
|  | Code value | Code value | Code value | Code value |
| 0 | - | 0 | - | 0 |
| 1 | - | 3277 | - | 1382 |
| 2 | - | 6554 | - | 2765 |
| 3 | - | 9830 | - | 4147 |
| 4 | 0 | 13107 | 0 | 5530 |
| 5 | 4096 | 16384 | 1728 | 6912 |
| 6 | 8192 | 19661 | 3456 | 8294 |
| 7 | 12288 | 22937 | 5184 | 9677 |
| 8 | 16384 | 26214 | 6912 | 11059 |
| 9 | 20479 | 29491 | 8640 | 12442 |
| 10 | 24575 | 32768 | 10368 | 13824 |
| 11 | 28671 | 36044 | 12096 | 15206 |
| 12 | 32767 | 39321 | 13824 | 16589 |
| 13 | 36863 | 42598 | 15552 | 17971 |
| 14 | 40959 | 45875 | 17280 | 19354 |
| 15 | 45055 | 49151 | 19008 | 20736 |
| 16 | 49151 | 52428 | 20736 | 22118 |
| 17 | 53247 | 55705 | 22464 | 23501 |
| 18 | 57343 | 58982 | 24192 | 24883 |
| 19 | 61439 | 62258 | 25920 | 26266 |
| 20 | 65535 | 65535 | 27648 | 27648 |
| 20.19 | - | - | 28034 | 27917 |
| 20.24 | - | - | 28085 | 27986 |
| Code value formula | Code value =65535/16*current-16384 | Code value =(65535/20)*current | Code value =(27648/16)*current-6912 | Code value =(27648/20)*current |

Notes: ① When the measuring range of current input module is 4mA~20mA(0~65535), it will support the functions of upper and lower overflow and upper overflow alarm, that is, when the channel input current is more than 20.03mA, the maximum code value of 65535 will be displayed and an alarm will be given; when the channel input current is less than 4mA, the minimum code value of 0 will be displayed.

(2) When the measuring range of current input module is 0mA~20mA (0~65535), it will support the functions of upper and lower overflow and upper overflow alarm, that is, when the channel input current is more than 20.03mA, the maximum code value of 65535 will be displayed and an alarm will be given; when the channel input current is less than 0mA, the minimum code value of 0 will be displayed.

③ When the measuring range of current input module is 4mA~20mA(0~27648), it will support the functions of upper overflow overshoot, upper and lower overflow and upper overflow alarm. The overshoot means that the channel input current will enter the overshoot when it exceeds the range, and the normal calculation code value will be displayed within the range of 4mA~20.24mA. The upper overflow means that when the channel input current is more than 20.24mA, the maximum overshoot code value of 28085 will be displayed and an alarm will be given. The lower overflow means that when the channel input current is less than 4mA, the minimum overshoot code value of 0 will be displayed.

④ When the measuring range of current input module is 0mA~20mA(0~27648), it will support the functions of upper overflow overshoot, upper and lower overflow and upper overflow alarm. The overshoot means that the channel input current will enter the overshoot when it exceeds the range, and the normal calculation code value will be displayed within the range of 0mA~20.24mA. The upper overflow means that when the channel input current is more than 20.24mA, the maximum overshoot code value of 27986 will be displayed and an alarm will be given. The lower overflow means that when the channel input current is less than 0mA, the minimum overshoot code value of 0 will be displayed.

      - Current output code value table

| Measuring range Current | 4mA~20mA | 0mA~20mA | 4mA~20mA | 0mA~20mA |
| --- | --- | --- | --- | --- |
|  | 0~65535 | 0~65535 | 0~27648 | 0~27648 |
|  | Code value | Code value | Code value | Code value |
| 0 | - | 0 | - | 0 |
| 1 | - | 3277 | - | 1382 |
| 2 | - | 6554 | - | 2765 |
| 3 | - | 9830 | - | 4147 |
| 4 | 0 | 13107 | 0 | 5530 |
| 5 | 4096 | 16384 | 1728 | 6912 |
| 6 | 8192 | 19661 | 3456 | 8294 |
| 7 | 12288 | 22937 | 5184 | 9677 |
| 8 | 16384 | 26214 | 6912 | 11059 |
| 9 | 20479 | 29491 | 8640 | 12442 |
| 10 | 24575 | 32768 | 10368 | 13824 |
| 11 | 28671 | 36044 | 12096 | 15206 |
| 12 | 32767 | 39321 | 13824 | 16589 |
| 13 | 36863 | 42598 | 15552 | 17971 |
| 14 | 40959 | 45875 | 17280 | 19354 |
| 15 | 45055 | 49151 | 19008 | 20736 |
| 16 | 49151 | 52428 | 20736 | 22118 |
| 17 | 53247 | 55705 | 22464 | 23501 |
| 18 | 57343 | 58982 | 24192 | 24883 |
| 19 | 61439 | 62258 | 25920 | 26266 |
| 20 | 65535 | 65535 | 27648 | 27648 |
| 22.81 | - | - | 32511 | 31538 |
| 23.52 | - | - | - | 32511 |
| Code value formula | Code value =65535/16*Current-16384 | Code value =(65535/20)*Current | Code value =(27648/16)*Current-6912 | Code value =(27648/20)*Current |

Note: ① When the measuring range of current output module is 4mA~20mA(0~27648) and 0mA~20mA(0~27648), it will supports the functions of upper overflow overshoot, upper overflow and upper overflow alarm, that is, when the measuring range of current output module is 4mA~20mA(0~27648) and the code value is set to be more than 32511, all channels will output the current of 22.81mA and give an alarm; when the measuring range of current output module is 0mA~20mA (0~27648) and the code value is set to be more than 32511, all channels will output the current of 23.52mA and give an alarm.

Wiring diagram

SRR3214

*COM internal conduction, PE internal conduction

* Shielded twisted pair is recommended for signal cables

SRR3234

*COM internal conduction, PE internal conduction

* Shielded twisted pair is recommended for signal cables

SRR4014

*COM internal conduction, PE internal conduction

* Shielded twisted pair is recommended for signal cables

SRR4034

*COM internal conduction, PE internal conduction

* Shielded twisted pair is recommended for signal cables

Overall dimension drawing

4 channels Dimensions of analog I/O terminal (mm)

Terminal cover

Overall dimension drawing

Dimensions of terminal cover (mm)

Note: DIN 35 mm standard guide rails are used for installation, with the dimensions of 35*7.5*1.0 and 35*15*1.0 (mm).

Installation and Removal

Installation guide

Precautions for installation\removal

- The protection level of the module is IP20. The module shall be installed in the cabinet for indoor use.

- The cabinet shall be provided with good ventilation measures (such as, an exhaust fan).

- Do not install this device next to or above the device that may cause overheating.

- Must install the module vertically on the fixed guide rail and keep the surrounding air circulation (there shall be at least 50mm space above and below the module for air circulation).

- Carry out the installation\removal when the power supply is cut off.

- After the module is installed, the wiring shall be carried out below and above the device.

Caution

- If the device is not used in accordance with the user manual, the protection provided may be damaged.

Ensure that the module is installed vertically on the fixed guide rail.

Installation and removal steps

| Module installation and removal |  |
| --- | --- |
| Installation steps | 1. Install the coupler module on the fixed guide rail. |
|  | 2. Install the required I/O terminals or functional modules on the right side of the coupler module in turn. |
|  | 3. Install the terminal cover to complete the module assembly. |
| Removal steps | 1. Open the module buckle with a flat screwdriver. |
|  | 2. Pull out the module to be removed. |

Installation/removal schematic diagram

Installation of the coupler module

- Push the upper and lower clips of the coupler module outwards and align the module vertically with the guide rail slot, as shown in Figure ① below.

- Press the coupler module toward the guide rail; when you hear a “Click” sound, the module will be installed in place, as shown in Fig. ② below.

②

Installation of I/O terminal

- Install the required I/O terminals or functional modules one by one according to the above steps for installing the coupler module, and push them in place as shown in the Figs. ③,④  and⑤  ; when you hear a “Click” sound, the modules are installed in place.

③

④

⑤

Installation of the terminal cover

- Install the terminal cover on the right side of the last module, and align the slot side of the terminal cover with the guide rail. For the installation method, please refer to the installation method of I/O terminals; push the terminal cover into place, as shown in Fig. ⑥ below.

⑥

- After the terminal cover is installed, check whether the front of the whole module is smooth, and ensure that all modules and end cover are installed in place and the front is flush, as shown in Fig. ⑦ below.

⑦

Removal

- Insert the flat screwdriver into the buckle of the module to be removed, and apply a force (hear noise) in the direction of the module, as shown in Fig, ⑧ below.

- Note: There is a buckle under each IO module. Please operate in the same way.

⑧

- Remove the module in the reverse operation of installing the module, as shown in the Fig. ⑨ below.

⑨

Wiring

Wiring terminal

Caution

| Wiring terminal |  |  |
| --- | --- | --- |
| Power terminal | Rated voltage | 250V |
|  | Rated current | 8A |
|  | Number of pins | 6P |
|  | Wire diameter | 24~16 AWG 0.2~1.5 mm² |
| Signal line terminals (input and output terminals) | Rated voltage | 150V |
|  | Rated current | 8A |
|  | Number of pins | 18P |
|  | Wire diameter | 28~16 AWG 0.2~1.5 mm² |
| Fieldbus ports | 2×RJ45 | Category 5 or above UTP or STP port (STP ports recommended) |

Wiring instructions and requirements

Precautions on the power wiring

- The power supplies on the module system side and the field side shall be configured and used separately; do not mix them.

- PE shall be grounded reliably.

Wiring tool requirements

The power terminal and signal line terminal are designed without screws, and all wires can be installed and removed with a flat screwdriver (with a size of ≤3mm).

Wire stripping length requirements

The recommended wire stripping length for power and signal line terminals is 10 mm.

Wiring methods

The single-stranded hard wires shall be stripped to the corresponding length, and directly inserted into the corresponding terminal holes by pressing the button.

The multi-strand flexible wires shall be stripped to the corresponding length, directly connected or matched with cold-pressed terminals (for reference sizes of tubular insulation terminals, please see the following table) and then insulated directly into the corresponding end holes by pressing the button.

The sizes of power terminals and signal line terminals are shown in the following table:

| Tubular insulation terminal size table |  |  |
| --- | --- | --- |
| Size requirements | Model | Wire cross-sectional area (mm2). |
| The length L of the tubular insulated terminal is 10mm. | E0310 | 0.3 |
|  | E0510 | 0.5 |
|  | E7510 | 0.75 |
|  | E1010 | 1.0 |
|  | E1510 | 1.5 |

Caution

- Only copper wires can be used for wiring conductors.

Caution

- The cable temperature shall be 80℃.

Usages

Description of parameters

Digital input filtering

The digital input filtering is used to prevent unexpected rapid changes in the program response input signal, which may be caused by switch contact jumping or electrical noise. The digital input filtering supports single module setting, each module can be configured separately, but the channels cannot be configured separately.

At present, the default digital input FilterTime is 3ms, and the supported setting ranges are no filtering, 0.1ms, 0.2ms, 0.5ms, 1ms, 2ms, 3ms (factory setting), 4ms...18ms, 19ms and 20ms. When it is 3ms, the stray waves within 3ms can be filtered. The input filtering time of 3ms means that a single signal changes from "0" to "1" or from "1" to "0" for 3ms before it can be detected, while a single high pulse or low pulse shorter than 3ms will not be detected.

Function description: When the input filtering time is 1ms, the stray waves within 1ms can be filtered. As shown below, when a signal of 250us is input, it will be regarded as an invalid signal, and a single high pulse or low pulse shorter than 1ms will not be detected, while the signals longer than 1ms can be collected.

1ms Valid signal

Invalid signal 250us

Input signal

Output sigal

Digital output signal clearing/holding

The clearing/holding function is used for modules with output channels. This function can be configured for the output mode of the output channels when the module is in non-OP state (when the operation stops or the coupler network cable is disconnected). This parameter supports the following output states:

Clear the output: When the communication is disconnected, the output will be automatically cleared in the module output channel, that is, output 0.

Output a valid value: When communication is disconnected, the valid value will be output in the module output channel, that is, output 1.

Hold the last output value: when the communication is disconnected, the last output value will be held in the module output channel.

The digital clearing and holding function supports the overall setting of the module (template mode) and the single channel setting (single channel mode). Any channel can be set in single channel mode or template mode, and the single channel mode has higher priority than the template mode. The specific configuration method is shown in the following table. By default, the output will be cleared as a whole.

| Clearing/holding parameters of digital output module |  |  |  |
| --- | --- | --- | --- |
| Parameter name | Parameter meaning | Parameter options | Default value |
| Template Mode | Template mode | Preset Low: Clear the output, that is, output 0 | Preset Low |
|  |  | Preset High: Output a valid value, that is, output 1 |  |
|  |  | Keep Mode: Hold the last output value |  |
| Channel x Mode Enable | Single channel mode | Template Value: Template mode value, that is, the single channel mode is not enabled | Follow Template |
|  |  | Preset Low: Clear the output, that is, output 0 |  |
|  |  | Preset High: Output a valid value, that is, output 1 |  |
|  |  | Keep Mode: Hold the last output value |  |

Digital input value when the module fails

When a module fails, the input value of the digital input module can be preset as needed, and you can choose to input 0 or keep the last input value.

Analog range setting

The analog range setting Range Select is used to set the measuring range of analog, and each channel can be configured separately (see Sections 3.3.4 and 3.3.5 “Analog parameters” for the range).

Analog input filtering

- Analog input filtering function

The analog input filter is used to average the data after A/D conversion internally, to reduce the fluctuation influence of the input signal caused by the noise.

The analog input is moved and averaged with specified A/D conversion times.

- Filtering function configuration

Each channel can be configured separately, ranging from 1 ~ 200, with a default of 10 times.

    - Analog output signal clearing/holding

The clearing/holding function is used for modules with output channels. This function can be configured for the output mode of the output channels when the module is in non-OP state (when the operation stops or the coupler network cable is disconnected). This parameter supports the following output states:

Clear the output: When the communication is disconnected, the output will be automatically cleared in the module output channel.

Hold the output: When communication is disconnected, the output will be held in the module output channel.

Output a preset value: when the communication is disconnected, the preset value will be output in the module output channel.

The analog clearing and holding function supports the overall setting (template mode) and the single channel setting (single channel mode) of the module. Any channel can be set in single channel mode or template mode, and the single channel mode has higher priority than the template mode. The specific configuration method is shown in the following table. By default, the output will be cleared as a whole

| Clearing/holding parameters of analog output module |  |  |  |
| --- | --- | --- | --- |
| Parameter name | Parameter meaning | Parameter value meaning | Default value |
| Template Setting | Template mode | Clear: Clear the outputs in all channels | Hold |
|  |  | Hold: Hold the output in all channels |  |
|  |  | Preset: Output the preset value in all channels |  |
| Channel x Abnormal Output | Single channel clearing/holding mode | Follow Template template mode value, that is, single channel mode is not enabled | Preset |
|  |  | Clear: Clear the output in the single channel |  |
|  |  | Hold: Hold the output in the single channel |  |
|  |  | Preset: Output the preset value in the single channel |  |
| Channel x Default Value Config | Setting of the preset value in single channel | Output the current/voltage value corresponding to code value (corresponding to the range code value table) | 0 |

Note: When the overall setting of the module (template mode) is set to Preset, that is, the preset values output in all channels are valid, the preset value shall be based on that of Channel 0 in the single-channel preset values, and the all-channel output will be performed.

    - Analog value power-off preservation

The analog parameters support the function of saving all configuration parameters of the module when communication is disconnected due to abnormal power failure, and the analog modules support the power failure saving function by default.

Coupler parameters

Alarm function settings

In the parameters of the coupler module, you can set whether the alarm function is enabled or not, and the alarm function is enabled by default.

PLC stop status output control

In the coupler module parameters, you can set the output status of DO (digital output) and DO (analog output) when the PLC is stopped, as shown in the following table:

| PLC stop status output control |  |  |
| --- | --- | --- |
| Parameter name | Parameter value meaning | Default value |
| PLC stop state DO control | Hold output | Hold |
|  | Output Clear 0 means clear output to 0 |  |
|  | Output Set 1 means set output to 1 |  |
| PLC stop state AO control | Hold output | Hold |
|  | Output Clear 0 means clear output to 0 |  |

In this user manual, the parameter configuration method of the combination of SRR8300 couplers +I/O terminals is introduced withTIA Portal V17 as an example. For specific steps, please see Section 6.5.1 “Parameter settings”. After modification, it is recommended to power on the device again.

Alarm Function

    - General fault codes of coupler

| No. | Error type | Error code | Event name | Event code (2#) | Event code (10 #) | Event code (16 #) | troubleshooting |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 2 | Online upgrade error | 1 | The firmware upgrade is abnormal | 0000000010000001 | 129 | 0x0081 | Upgrade it again, and check whether there is interference in the environment and whether the firmware is too large |
|  |  | 2 | The firmware does not match the current module model | 0000000010000010 | 130 | 0x0082 | Check whether the file is correct, and whether there is abnormality or interference in the module |
| 3 | Voltage error | 5 | The voltage on the load side is not applied | 0000000011000101 | 197 | 0x00C5 | Check whether the power supply on the field side is connected |
| 6 | Channel error | 4 | There is channel upper or lower overflow | 0000000110000100 | 388 | 0x0184 | Check whether the input signal of the corresponding channel is beyond the measuring range and whether the output signal is beyond the configurable range |
| 7 | Parameter error | 0 | The parameter setting is abnormal | 0000000111000000 | 448 | 0x01C0 | Check the module parameter setting |
| 63 | Communication error | 1 | The initialization fails | 0000111111000001 | 4033 | 0x0FC1 | Check whether the module is connected normally |
|  |  | 2 | The token is timeout | 0000111111000010 | 4034 | 0x0FC2 | Check whether there is abnormality or interference in the module |
|  |  | 3 | The module runs offline | 0000111111000011 | 4035 | 0x0FC3 | Check whether the module is online or there is interference |
|  |  | 4 | The parsing data CRC is error | 0000111111000100 | 4036 | 0x0FC4 | Check whether there is abnormality or interference in the module |

Viewing fault codes

Taking TIA Portal V17 as an example, when a device fails during project operation, click the wrench icon on the right side of the device name at the bottom of the project tree to view the detailed diagnostic status and alarm information.

MRP ring network redundancy

PROFINET's Media Redundancy mechanism ensures the uptime of the entire system in the event of a disconnection/connection failure somewhere in the PROFINET network. The typical reconfiguration time is 200ms and supports up to 50 devices per ring.

Media redundancy is achieved by transforming a linear network topology into a ring network topology, in which there is a redundancy manager and the other nodes (PROFINET IO controllers/devices) are called redundant clients. In the event of a disconnection/connection failure somewhere in the PROFINET network, the redundancy manager detects the failure and rebuilds the interrupted network so that the system continues to operate.

The media redundant network structure has the following advantages:

- The media redundancy structure significantly increases the availability of the equipment, since the failure of a single device has no impact on communication.

- The required repair work can be carried out without any time pressure, as there is no need for the plant to shut down during the repair process.

- n the event of a network failure, rapid network diagnostics and faster troubleshooting.

- In the event of a breakdown, the cost due to production stoppage is reduced.

Configuring MRP Ring Network Rules:

- All points must support MRP and the MRP protocol must be enabled.

- All devices must be interconnected through ring ports.

- All devices in the ring network belong to the same redundancy domain.

- Up to 50 devices can be connected in a ring network, otherwise the reassembly time will exceed 200ms.

- One device in the ring network can be used as a redundancy manager, and the other devices are redundant clients.

- All partner ports within the ring have the same settings.

The MRP network reconstruction time is 200 ms, and the I/O communication is interrupted during the reconfiguration. Therefore, to ensure that no I/O drops occur during network reconfiguration and faults are reported, you need to set the watchdog time of the I/O device to more than 200 ms.

For details about how to operate the media redundancy function, see the introduction to ring network redundancy configuration in section 6.5.2.

Hardware detection

The module supports Siemens TIA Portal automation software to automatically scan the IO module. For details, see Section 6.5.1 for Hardware Detection and Adding Devices.

Configuration application of PROFINET coupler

    - Application in TIA Portal V17 software environment

- Preparation

- Hardware environment

- Module preparation, with SRR8300+SRR1016+SRR2116+SRR3214+SRR4034 topology as an example

- 1 computer, with TIA Portal V17 software pre-installed

- 1 Siemens PLC, this description uses the Siemens S7-1200 CPU 1212C DC/DC/DC as an example

- special shielded cable

- 1 switching power supply

- Device configuration file

Please contact our company`s staff for the configuration file.

- Hardware configuration and wiring

Please follow the requirements of Section 4 “Installation and removal” and Section 5 “Wiring”.

- Create a new project

- Open the TIA Portal V17 software, click "Create New Project", and click the "Create" button after the information is entered, as shown in the following figure.

- Project Name: user-defined, may be default.

- Path:project path, may be default.

- Version: maybe default.

- Author: maybe default.

- Note: user-defined, optional.

- Add PLC controller

- Click "Configure Device", as shown in the following figure.

- Click “Add New Device”, select current PLC model, and click Add, as shown in the following figure. After the addition is complete, you can view that the PLC has been added to the device navigation tree.

- Scan for connected devices

- Click Online Access -> Update Accessible Devices in the navigation tree on the left, as shown in the following figure. After the update is complete, the connected slave devices are displayed, as shown in the following image.

The computer's IP address must be in the same network segment as the PLC. If not, change the computer's IP address and repeat the above steps.

- Add a GSD profile

- In the menu bar, select "Options -> Manage General Station Description File (GSDML) (D)", as shown in the figure below.

- Click "Source Path" to select a folder and check whether the status of the GSD file to be added is "Not Installed". If it is not installed, click the "Install" button. If it is already installed, click "Cancel" to skip the installation steps, as shown in the following figure.

- Hardware detection to add devices

- Double-click "Device and Network" in the left navigation tree and select PLC in the network view, as shown in the figure below.

- In the menu bar, select "Online -> Hardware Detection -> PROFINET Devices in Network", as shown in the following figure.

- A hardware detection window pops up. Select the correct PG/PC interface and click “Start Search”, as shown in the figure below.

- Detect coupler devices on the network, select couplers, and click Add Device, as shown in the following figure.

- After the coupler is added successfully, you can see the coupler icon in the network view, as shown in the figure below.

- Select the coupler icon and switch to the device view. You can see that all IO devices in the topology have been detected and added, as shown in the following figure.

- Manually add a slave device

In addition to the method of adding devices through hardware detection, you can also add them manually, as described below.

- Double-click "Devices & Networks" in the left navigation bar.

- Click the vertical button of "Hardware Catalog" on the right, and the catalog will be displayed as shown in the figure below.

- Select "Other field devices -> PROFINET IO -> I/O -> SINSEGYE -> SRR8300", drag or double-click SRR8300 to "Network View", as shown in the following figure.

- Switch to the network view, click "Unassigned (blue font)" on the coupler or slave device, and select "PLC_1.PROFINET Interface_1", as shown in the figure below.

- After the connection is completed, it will be as shown in the figure below.

- Click the device name to rename the device, as shown in the following figure.

- Click "Device View" to enter the device overview of the coupler. Under "Hardware Catalog" on the right, add modules in sequence according to the actual topology (the order must be consistent with the actual topology, otherwise communication will not be successful), as shown in the following figure.

- Assign a Device Name

- In the network view, right-click the connection line between the PLC and the coupler and select "Assign Device Name", as shown in the figure below.

- The "Assign PROFINET Device Name" window pops up, as shown below.

- Select PLC as the device name and click "Update List". After the update is completed, it will be as shown in the figure below.

- Check whether the node status in Accessible Nodes in Network is OK. If it is not OK, select the device and click Assign Name, as shown in the following figure.

- Select Coupler in the device name, click Update List, and assign names using the same method after updating, as shown in the figure below.

- Check whether the MAC address on the module silk screen is the same as the MAC address of the assigned device name. Click Close.

- Downloading the configuration structure

- In the network view, select the PLC. First click the Compile button in the menu bar, then click the Download button to download the current configuration to the PLC.

- In the pop-up "Extended Download to Device" interface, configure as shown below.

- Click the Start Search button as shown in the following figure.

- Click "Download" and the download preview window will pop up, as shown in the figure below.

- Click "Load".

- Click "Finish".

- Restart the device.

- Communication connection

- Click the "Start CPU" button in the menu bar, and then click the "Go Online" button. If both icons are green, the connection is successful, as shown in the figure below.

- Parameter settings

- In offline state, open the "Network View", select the coupler module, switch to the device view, right-click the SRR1016 module, and click the "Properties" button to view and set the module parameters, as shown in the figure below.

- On the SRR1016 property page, click "Module Parameters", as shown in the figure below. The parameters can be configured according to actual needs. After the configuration is completed, re-download the program to the PLC, and the PLC and the module need to be powered on again.

- Use the same method to view the property page of SRR2116 and click "Module Parameters", as shown in the figure below. The parameters can be configured according to actual needs. After the configuration is completed, re-download the program to the PLC, and the PLC and the module need to be powered on again.

- Right-click the SRR3214 module and click the "Properties" button to view and set the module parameters, as shown in the figure below.

- On the SRR3214 property page, click "Module Parameters", as shown in the figure below. The parameters can be configured according to actual needs. After the configuration is completed, re-download the program to the PLC, and the PLC and the module need to be powered on again.

- On the SRR4034 property page, click "Module Parameters", as shown in the figure below. The parameters can be configured according to actual needs. After the configuration is completed, re-download the program to the PLC, and the PLC and the module need to be powered on again.

- Right-click the coupler icon in the network view and click the "Properties" button to view and set the parameters of the coupler, as shown in the figure below.

- On the coupler properties page, click "Module Parameters", as shown in the figure below. The two parameters of whether the alarm function is enabled or not and the output control of AO and DO in the PLC stop state can be configured according to actual needs. After the configuration is completed, re-download the program to the PLC, and the PLC and the module need to be powered on again.

- Functional validation

- Expand the project navigation on the left, select "Monitoring and Enforcement Tables", double-click "Add New Monitoring Table", and the system will add a new monitoring table, as shown in the figure below.

b. Open the "Device View" and check the channel I address (channel address of input signal) and Q address (channel address of output signal) of each module in the device overview.

For example, the "I address" of the SRR1016 module is 1 to 2, and the "Q address" of the SRR2116 module is 1 to 2, as shown in the figure below.

- Fill in the input and output channel addresses in the address cells of the monitoring table, such as writing "IB1" to "IB2", "QB1" to "QB2", and press the "Enter key". After all are filled in, click the button to monitor the data, as shown in the figure below.

- Taking the input channel 0 and channel 1 of the SRR1016 module as an example, when the module input channel 0 and channel 1 have valid voltage input, it can be observed in the monitoring value cell of the monitoring table; the SRR2116 output channel can be forced to output control by modifying the monitoring value, as shown in the figure below.

- Taking channel 0 of the SRR3214 module as an example, when there is voltage input to channel 0, the input voltage code value can be monitored in the monitoring table, as shown in the figure below. For details on the correspondence between the code value and voltage, see 3.3.4 Analog Voltage Parameters.

- Taking channel 0 of the SRR4034 module as an example. If you want channel 0 to output, you can enter a value in the modification value cell of the monitoring table. The corresponding relationship between the code value and the current is detailed in 3.3.5 Analog Current Parameters. Click Write and you can see that the corresponding channel light is on, as shown in the figure below.

Ring network redundancy configuration application

- Preparation

- Hardware environment

- Module preparation. This description takes the SRR8300+SRR8300+SRR8300+SRR8300 network topology as an example.

- 1 computer with TIA Portal V17 software pre-installed

- 1 Siemens PLC,This description takes Siemens S7-1500 CPU 1511-1 PN as an example

- special shielded cable

- 1 switching power supply

- Device configuration file

Please contact our company`s staff for the configuration file.

- Hardware configuration and wiring

Please follow the requirements of Section 4 “Installation and removal” and Section 5 “Wiring”.

- Ring redundancy

- Create a project in TIA Portal V17 software and add the PLC+SRR8300+SRR8300+SRR8300+SRR8300 network topology to the network configuration. The steps for configuring the file and adding devices are the same as those in section 6.5.1.

- Create a topology configuration in the topology view, connect the two interfaces of each device end to end, and configure a ring network topology, as shown in the following figure.

- Assign a device name to each device (PLC and coupler) in the network view.

- Set the IO cycle for each device (PLC and coupler). Taking the coupler as an example, right-click the coupler icon in the network view, click the "Properties" button, find the watchdog time setting in the IO cycle, and set the watchdog time to 200ms, as shown in the figure below.

- Highlight the Sync Domain in the Network view and click Sync Domain Network to enter Domain Management, as shown in the following figure.

- On the MRP domain management page, assign the MRP role and ring network port to each device. In this example, set the PLC as the manager and the coupler as the client, as shown in the following figure.

- After compiling and downloading the program, enter the online topology view to check whether the device status is normal.

- Check the diagnostic interrupt function, and a diagnostic interrupt will be generated when the wiring or port on the ring network port is wrong or the ring network is disconnected, as shown in the figure below.

- In the topology view, when a port error or device failure occurs, you can quickly view the fault point.