Manual of

SRR Series Plug-in I/O Products (EtherCAT Coupler)

SINSEGYE (Shenzhen) Computer System Co., Ltd.

V1.0

Contents

1 Product Overview	1

1.1 Product introduction	1

1.2 Product features	1

1.3 Application mode	2

2 List of Modules	3

2.1 List of Modules	3

3 Introduction of Modules	4

3.1 EtherCAT coupler	4

3.1.1 Panel structure	4

3.1.2 Indicator functions	5

3.1.3 Technical specifications	6

3.1.3.1 Port parameters	6

3.1.3.2 Power parameters	6

3.1.3.3 General parameters	6

3.1.4 Power wiring diagram	7

3.1.5 Fieldbus wiring	8

3.1.6 Overall dimension drawing	9

3.2 Digital I/O terminal	10

3.2.1 Indicator functions	10

3.2.2 Technical specifications	10

3.2.2.1 Digital input module parameters	10

3.2.2.2 Digital output module parameters	11

3.2.2.3 General technical parameters	11

3.2.3 Wiring diagram	12

3.2.3.1 SRR1016	12

3.2.3.2 SRR2116	13

3.2.3.3 SRR2216	14

3.2.4 Outline dimension drawing	15

3.3Analog I/O terminal	16

3.3.1 Indicator functions	16

3.3.2 Technical specifications	16

3.3.2.1 Analog input module parameters	16

3.3.2.2 Analog output module parameters	17

3.3.2.3 General technical parameters	17

3.3.3 Analog voltage parameters	18

3.3.3.1 Voltage input range selection table	18

3.3.3.2 Voltage output range selection table	18

3.3.3.3 Voltage input code value table	19

3.3.3.4Voltage output code value table	21

3.3.4 Analog current parameters	22

3.3.4.1Current input range selection table	22

3.3.4.2 Current output range selection table	22

3.3.4.3 Current input code value table	23

3.3.4.4 Current output code value table	24

3.3.5 Wiring diagram	25

3.3.5.1 SRR3214	25

3.3.5.2 SRR3234	26

3.3.5.3 SRR4014	27

3.3.5.4 SRR4034	28

3.3.6 Overall dimension drawing	29

3.4 Terminal cover	30

3.4.1 Overall dimension drawing	30

4 Installation and Removal	31

4.1 Installation guide	31

4.2 Installation and removal steps	32

4.3 Installation/removal schematic diagram	33

5 Wiring	38

5.1Wiring terminal	38

5.2 Wiring instructions and requirements	38

6 Usages	40

6.1 Description of parameters	40

6.1.1 Digital input filtering	40

6.1.2 Digital output signal clearing/holding	41

6.1.3 Analog range setting	41

6.1.4 Analog input filtering	41

6.1.5 Analog output signal clearing/holding		42

6.1.6 Analog value power-off preservation	42

6.2 Fault code information	43

6.2.1 General fault codes of coupler	43

6.2.2 Viewing fault codes	44

6.3  Configuration application of  EtherCAT coupler	45

6.3.1 Application in Sysmac Studio software environment	45

6.4 Online upgrade of firmware	61

Product Overview

Product introduction

The SRR series plug-in I/O terminal is a combination structure of couplers and I/O terminals. The coupler is used to connect the extensible I/O terminal to the real-time industrial Ethernet system, and the S-Link fieldbus is used on the backplane. The coupler module is used for the communication of the fieldbus, to realize the real-time data exchange function between various I/O terminals and the couplers/controllers.

The SRR series plug-in I/O terminal has rich varieties and high real-time performance, which can provide the supports for users to collect data at high speed, optimize system configuration, simplify field wiring and improve system reliability.

Product features

- Less occupied nodes

A node consists of a fieldbus coupler, 1~32 SRR series I/O terminals and a terminal cover.

- Rich functional expansion

It supports flexible expansion and complete I/O terminal types, and can integrate various digital modules and analog modules to meet the needs of different applications.

- Flexible configuration

Various types of plug-in I/O terminals can be combined flexibly.

- Strong compatibility

The communication ports of couplers meet the communication standard and support the mainstream EtherCAT master station.

- Small volume

It has compact structure and small occupied space.

- Easy diagnosis

The indicators are complete, the module status is clear and the test and maintenance are convenient.

- High speed

The S-Link fieldbus is used on the backplane, with the minimum scanning cycle of 200 us, and the typical value of 1 ms.

- Easy installation

It is installed with DIN 35 mm standard guide rail.

The elastic terminal is used, to ensure convenient and quick wiring.

Application mode

The coupler module is connected with the controller in the application site, and the I/O terminal is used to connect the input and output sensors in the application site. Usually, the process of data acquisition and processing control is as follows:

A.The input I/O terminals collect various signals on site and sent them the coupler via the internal fieldbus;

B.The controller reads the data from the coupler via the fieldbus or industrial Ethernet, processes the data, and then writes the output data into the coupler;

- C.The coupler writes the output data to the output I/O terminals via the internal fieldbus, to control the device.

The extensible I/O terminals include digital input module, digital output module, analog input module and analog output module.

Application mode: Use the combination application mode of coupler, digital, analog and other modules.

Application configuration: It can adapt to the combination configuration of different models of I/O terminals according to the requirements of master station access capacity, number of stations, I/O points, and function types.

Configuration rules: Coupler module, I/O terminals, terminal cover are configured from left to right.

The combination application mode of coupler, I/O terminals and terminal cover is used in the product, including the following combinations.

Combination mode I (coupler module, I/O terminals and terminal cover)

List of Modules

List of modules

| Model | Product description |  |
| --- | --- | --- |
| SRR8200 | EtherCAT fieldbus coupler module |  |
| SRR1016 | 16-channel digital input module, input NPN/PNP compatible, input filtering time of 3 ms by default |  |
| SRR2116 | 16-channel digital output module, output NPN type |  |
| SRR2216 | 16-channel digital output module, output PNP type |  |
| SRR3214 | 4-channel analog voltage input module | Single-port signal with adjustable range: Disable, -10V~+10V, 0V~10V, -5V~+5V, 0V~5V and 1V~5V |
| SRR3234 | 4-channel analog current input module | Single-port signal with adjustable range: Disable, 4mA~20mA and 0mA~20mA |
| SRR4014 | 4-channel analog voltage output module | Single-port signal with adjustable range: Disable, -10V~+10V, 0V~10V, -5V~+5V, 0V~5V and 1V~5V |
| SRR4034 | 4-channel analog current output module | Single-port signal with adjustable range: Disable, 4mA~20mA and 0mA~20mA |
| SRR9010 | Terminal cover |  |

Introduction of Modules

EtherCAT coupler

Panel structure

| No. | Name | Description |
| --- | --- | --- |
| ① | Module indicator and indicator ID | Indicate the coupler power state and the system operation state |
| ② | Fieldbus port IN | RJ45 port |
| ③ | Fieldbus port OUT | RJ45 port |
| ④ | Power terminal | 6P snap-in wiring terminal |
| ⑤ | Guide rail slot | Fix DIN 35 mm guide rail |

Indicator functions

| Definition of EtherCAT coupler indicators |  |  |  |  |
| --- | --- | --- | --- | --- |
| ID | Name | Color | Status | Description |
| PWR | Power indicator | Green | ON | The module power supply is running normally |
|  |  |  | OFF | The power supply is not running or abnormal |
| OVR | Overload indicator | Red | OFF | No overloaded |
|  |  |  | ON | At more than 90% (±5%) of the load |
| RUN | EtherCAT running status indicator | Green | ON | EtherCAT OP status |
|  |  |  | Flash at 2.5Hz | EtherCAT PreOP status |
|  |  |  | Single flash (with a cycle of 200ms On and 1s Off) | EtherCAT SafeOP status |
|  |  |  | Flash at 10Hz | BootStrap status |
|  |  |  | OFF | EtherCAT Init status |
| ERR | EtherCAT fault indicator | Red | Double flashes [1] | EtherCAT watchdog timeout |
|  |  |  | Single flash (with a cycle of 200ms On and 1s Off) | Module local error |
|  |  |  | Flash at 2.5Hz | General configuration error |
|  |  |  | OFF | EtherCAT communication normality |
| IOR | IO communication indicator | Green | ON | I/O process data has been established |
|  |  |  | Flash at 1Hz | No business data interaction |
|  |  |  | Flash at 10Hz | Firmware upgrade of coupler |
| IOE | IO abnormal indicator | Red | ON | Communication abnormality |
|  |  |  | Flash at 1Hz | I/O terminal abnormality alarm |
|  |  |  | OFF | No communication abnormality |

Note [1]: Double flash means a cycle of 200ms ON & 200ms OFF and 200ms ON & 1000ms OFF.

| Definition of network status indicators |  |  |  |  |
| --- | --- | --- | --- | --- |
| ID | Name | Color | Status | Description |
| IN | Network status indicator IN | Orange | Flash | The connection is established and there is data interaction |
|  |  |  | OFF | There is no data interaction or there is an abnormality |
|  |  | Green | ON | The network connection is established |
|  |  |  | OFF | The network connection is not established or abnormal. |
| OUT | Network status indicator OUT | Orange | Flash | The connection is established and there is data interaction |
|  |  |  | OFF | There is no data interaction or there is an abnormality |
|  |  | Green | ON | The network connection is established |
|  |  |  | OFF | The network connection is not established or abnormal. |

Technical specifications

Port parameters

| EtherCAT port parameters |  |
| --- | --- |
| Fieldbus protocol | EtherCAT |
| Number of slave stations | Depends on the number of slave stations supported by the master station |
| Data transmission medium | Ethernet/EtherCAT CAT5 cable |
| Transmission rate | 100Mbps |
| Minimum cycle time [1] | 250us |
| Transmission distance | ≤100m (station-station distance) |
| Fieldbus port | 2×RJ45 |
| Maximum serial number of modules | 32 |
| Input and output process data volume | 1024Bytes [2] |

Note [1]: It refers to the cycle time between PLC and coupler (scanning cycle).

Note [2]: The total length of uplink and downlink data does not exceed 1024Bytes.

Power parameters

| Power parameters |  |
| --- | --- |
| Input voltage | SELV Input 24VDC（18V~36V） |
| Input current | Max：600mA（24VDC） |
| Backplane power current | Max：2A |
| Backplane power voltage | 5VDC |

General parameters

| General technical parameters |  |  |
| --- | --- | --- |
| Dimensions |  | 100x27.82x80mm |
| Mass |  | 95g |
| Operating environment | Operating temperature | -20℃~+60℃ |
|  | Storage temperature | -40℃~+80℃ |
|  | Relative humidity | 95%, no condensation |
|  | Altitude | ≤2000m |
|  | Protection grade | IP20 |
|  | Overvoltage category | I |
|  | Pollution level | Level 2 |
| Module abnormal self-recovery |  | Support |
| Access PDO via SDO |  | Support |
| Diagnosis |  | Support |
| Alarm |  | Support |
| Firmware upgrade |  | Support |
| Short circuit protection |  | support (automatic recovery mechanism) |
| Reverse connection protection |  | support (automatic recovery mechanism) |
| Surge protection |  | Support |

Power wiring diagram

Use the 24VDC power module, connect the power supply with the wiring method as shown below, and a reliably ground the PE (twisted pair is recommended for the power cable).

*24V internal conduction, 0V internal conduction.

Fieldbus wiring

Use standard RJ45 network port and standard crystal connector; the pin distribution is shown in the following table.

| Pin No. | Signal |
| --- | --- |
| 1 | TD+ |
| 2 | TD- |
| 3 | RD+ |
| 4 | 一 |
| 5 | 一 |
| 6 | RD- |
| 7 | 一 |
| 8 | 一 |

Notes

- It is recommended to use Category 5 or higher double shielded (woven net + aluminum foil) STP cable as communication cable.

- The length of cables between devices cannot exceed 100 m.

Overall dimension drawing

Dimensions of coupler (mm)

Digital I/O terminal

    - Indicator functions

| Definition of digital I/O terminal indicators |  |  |  |  |
| --- | --- | --- | --- | --- |
| ID | Name | Color | Status | Description |
| PWR | Power indicator | Green | ON | The power supply is normal |
|  |  |  | OFF | The product is not powered on or the power supply is abnormal |
| RUN | Running status indicator | Green | ON | The system is running normally |
|  |  |  | Flash at 1Hz | There is no business data interaction, which shall be established |
|  |  |  | Flash at 10Hz | Firmware upgrade |
|  |  |  | OFF | The system is not running |
| 0~7 | Input channel indicator | Green | ON | There is signal input in the module channel |
|  |  |  | OFF | There is no signal input or abnormal signal input in the module channel |
| 0~7 | Output channel indicator | Green | ON | There is signal input in the module channel |
|  |  |  | OFF | There is no signal input or abnormal signal input in the module channel |

    - Technical specifications

      - Digital input module parameters

| Digital input |  |
| --- | --- |
| Product model | SRR1016 |
| Rated voltage of fieldbus input power | 5VDC (4.5V ~ 5.5V) |
| Rated current of fieldbus input power | ≤50mA |
| Rated input voltage | 24 VDC (20.4 V ~ 28.8 V) |
| Typical input current | 5mA/ch (24 VDC) |
| Input signal points | 16 |
| Input signal type | NPN/PNP compatible |
| Input signal form | Voltage direct input forms Sink: NPN open collector input Source: PNP open collector input |
| OFF voltage /OFF current | Below -3V ~ +5V/0.9mA |
| ON voltage/ON current | Above 11V~30V/2.1mA |
| Response time | <50us |
| Input filtering | No filtering, 0.1ms, 0.2ms, 0.5ms, 1ms, 2ms, 3ms (factory setting), 4ms...18ms, 19ms, 20ms |
| Maximum input frequency | 150Hz (filtering time: 3ms) |
| Input impedance | 5.4KΩ |
| Isolation mode | Optocoupler isolation |
| Isolation withstand voltage | 500VAC |
| Rated current loss | 50mA |
| Power consumption | 0.25W |
| Digital input type | Type1/Type3 |
| Channel indicator | Green LED |

      - Digital output module parameters

| Digital output |  |  |
| --- | --- | --- |
| Product model | SRR2116 | SRR2216 |
| Rated voltage of fieldbus input power | 5VDC (4.5V ~ 5.5V) |  |
| Rated current of fieldbus input power | ≤75mA | ≤55mA |
| Input voltage range on the field side | 24 VDC (20.4 V ~ 28.8 V) |  |
| Output signal points | 16 | 16 |
| Output signal types | NPN | PNP |
| Output voltage drop | ＜1V |  |
| Output load types | Resistive load, inductive load and indicator load |  |
| Single-channel rated current | Max: 0.5A |  |
| Leakage current | <10uA |  |
| Response time | <150us |  |
| Output channel protection | Short circuit protection (automatic recovery mechanism) |  |
| Module protection | Reverse connection protection (automatic recovery mechanism), surge protection on the field side |  |
| Isolation mode | Optocoupler isolation |  |
| Isolation withstand voltage | 500VAC |  |
| Rated current loss | 75mA | 55mA |
| Power consumption | 0.375W | 0.275W |
| Channel indicator | Green LED |  |

      - General technical parameters

| General technical parameters |  |
| --- | --- |
| Dimensions | 100x16.11x80mm |
| Mass | 70g |
| Operating temperature | -20℃~+60℃ |
| Storage temperature | -40℃~+80℃ |
| Relative humidity | 95%, no condensation |
| Altitude | ≤2000m |
| Pollution level | Level 2 |
| Protection grade | IP20 |

    - Wiring diagram

      - SRR1016

*COM internal conduction; NPN/PNP compatible

      - SRR2116

      - SRR2216

    - Outline dimension drawing

Dimensions of digital I/O terminal (mm)

  - Analog I/O terminal

    - Indicator functions

| Definition of analog I/O terminal indicators |  |  |  |  |
| --- | --- | --- | --- | --- |
| ID | Name | Color | Status | Description |
| PWR | Power indicator | Green | ON | The power supply is normal |
|  |  |  | OFF | The product is not powered on or the power supply is abnormal |
| RUN | Running status indicator | Green | ON | The system is running normally |
|  |  |  | Flash at 1Hz | There is no business data interaction, which shall be established |
|  |  |  | Flash at 10Hz | Firmware upgrade |
|  |  |  | OFF | The system is not running |
| 0~7 | Input channel indicator | Green | ON | There is signal input in the module channel |
|  |  |  | OFF | There is no signal input or abnormal signal input in the module channel |
| 0~7 | Output channel indicator | Green | ON | There is signal input in the module channel |
|  |  |  | OFF | There is no signal input or abnormal signal input in the module channel |

    - Technical specifications

      - Analog input module parameters

| Analog input |  |  |
| --- | --- | --- |
| Product model | SRR3214 | SRR3234 |
| Rated voltage of fieldbus input power | 5VDC (4.5V ~ 5.5V) |  |
| Rated current of fieldbus input power | ≤145mA | ≤70mA |
| Input points | 4 | 4 |
| Input types | Voltage type | Current type |
| Input signals | Disable,-10V to+-10V~+10V to 10V, -5V~+5V, 0V~5V, 1V~5V (adjustable range, -10V~+10V by default) | Disable, 4mA~20mA and 0mA~20mA (adjustable range, 0mA~20mA by default) |
| Input signal type | Single-port signal |  |
| Channel response time | 230us/ch 380us/4ch | 230us/ch 300us/4ch |
| Resolution | 16bits |  |
| Sampling rate (all channels) | ≤1ksps |  |
| Accuracy | ±0.3%0.1% at 25℃; 0.3% within the whole temperature range |  |
| Input filtering | Support |  |
| Smoothing series | 1~200 |  |
| Input impedance (voltage type) | ≥400kΩ | - |
| Input impedance (current type) | - | ≤100Ω |
| Maximum allowable voltage of channel (voltage type) | 30V | - |
| Maximum allowable channel current (current type) | - | 30mA |
| No affect on the system | When the ±15V power supply is damaged and short-circuited, the system +5V power shall not be affected |  |
| Potential isolation | There is no isolation between channels, and there is isolation between channel and backplane fieldbus, and between channels and power voltage |  |
| Input overload protection | Support clamping protection | Support current limiting protection |
| Input protection | ±30V | ±30mA |
| Isolation withstand voltage | 500VDC |  |
| Rated current loss | 145mA | 70mA |
| Power consumption | 0.725W | 0.35W |
| Channel indicator | Green LED |  |

      - Analog output module parameters

| Analog output |  |  |
| --- | --- | --- |
| Product model | SRR4014 | SRR4034 |
| Rated voltage of fieldbus input power | 5VDC (4.5V ~ 5.5V) |  |
| Rated current of fieldbus input power | ≤30mA |  |
| Input voltage range on the field side | 24 VDC (20.4 V ~ 28.8 V) |  |
| Output points | 4 | 4 |
| Output types | Voltage type | Current type |
| Output signals | Disable,-10V to+-10V~+10V to 10V, -5V~+5V, 0V~5V and 1V~5V (adjustable range, -10V~+10V by default) | Disable, 4mA~20mA and 0mA~20mA (adjustable range, 0mA~20mA by default) |
| Channel response time | 200us/ch 200us/4ch |  |
| Resolution | 16bits |  |
| Accuracy | 0.1% at 25℃; 0.3% within the whole temperature range |  |
| Load impedance (voltage type) | ≥ 2kΩ (1kΩ accuracy: 3 % at 25℃; 5 ‰ with the whole temperature range) | - |
| Load impedance (current type) | - | ≤500Ω |
| No affect on the system | When the ±15V power supply is damaged and short-circuited, the system +5V power supply shall not be affected |  |
| Output protection | Overload protection, open circuit protection and short circuit protection (with automatic recovery mechanisms) |  |
| Potential isolation | There is no isolation between channels, and there is isolation between channel and backplane fieldbus, and between channel and power voltage |  |
| Isolation withstand voltage | 500VDC |  |
| Rated current loss | 30mA |  |
| Power consumption | 0.15W |  |
| Optional clearing/holding functions in non-OP state | Support |  |
| Channel indicator | Green LED |  |

      - General technical parameters

| General technical parameters |  |
| --- | --- |
| Dimensions | 100 x16.11 x 80mm |
| Mass | 70g |
| Operating temperature | -20℃~+60℃ |
| Storage temperature | -40℃~+80℃ |
| Relative humidity | 95%, no condensation |
| Altitude | ≤2000m |
| Pollution level | Level 2 |
| Protection grade | IP20 |

    - Analog voltage parameters

      - Voltage input range selection table

| Voltage input range selection and code value range |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Range selection | Measuring range | Code value range | Voltage input calculation formula | Voltage output calculation formula | Code value correspondence table |
| 0 | Disable, indicating that the channel is not enabled |  |  |  |  |
| 1 (by default) | -10V~+10V | -32768~32767 | D=(65535/20)*U | U=(D*20)/65535 | See Section 3.3.4.3 “Voltage input code value table” |
| 2 | 0V~10V | 0~32767 | D=(32767/10)*U | U=(D*10)/32767 |  |
| 3 | -10V~+10V | -27648~27648 | D=(55296/20)*U | U=(D*20)/55296 |  |
| 4 | 0V~10V | 0~27648 | D=(27648/10)*U | U=(D*10)/27648 |  |
| 5 | -5V~+5V | -27648~27648 | D=(55296/10)*U | U=(D*10)/55296 |  |
| 6 | 0V~5V | 0~27648 | D=(27648/5)*U | U=(D*5)/27648 |  |
| 7 | 1V~5V | 0~27648 | D=(27648/4)*U-6912 | U=(D+6912)*4/27648 |  |

Note: D represents code value, U represents voltage, and the default range of analog voltage input module is 1:-10V ~+10V (-32768 ~ 32767).

      - Voltage output range selection table

| Voltage output range selection and code value range |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Range selection | Measuring range | Code value range | Voltage input calculation formula | Voltage output calculation formula | Code value correspondence table |
| 0 | Disable, indicating that the channel is not enabled |  |  |  |  |
| 1 (by default) | -10V~+10V | -32768~32767 | D=(65535/20)*U | U=(D*20)/65535 | See Section 3.3.4.4 “Voltage output code value table” |
| 2 | 0V~10V | 0~32767 | D=(32767/10)*U | U=(D*10)/32767 |  |
| 3 | -10V~+10V | -27648~27648 | D=(55296/20)*U | U=(D*20)/55296 |  |
| 4 | 0V~10V | 0~27648 | D=(27648/10)*U | U=(D*10)/27648 |  |
| 5 | -5V~+5V | -27648~27648 | D=(55296/10)*U | U=(D*10)/55296 |  |
| 6 | 0V~5V | 0~27648 | D=(27648/5)*U | U=(D*5)/27648 |  |
| 7 | 1V~5V | 0~27648 | D=(27648/4)*U-6912 | U=(D+6912)*4/27648 |  |

Note: D represents code value, U represents voltage, and the default range of analog voltage output module is 1: -10V ~+10V (-32768 ~ 32767).

      - Voltage input code value table

| Measuring range Voltage | -10V~+10V | 0V~10V | -10V~+10V | 0V~10V |
| --- | --- | --- | --- | --- |
|  | -32768~32767 | 0~32767 | -27648~27648 | 0~27648 |
|  | Code value | Code value | Code value | Code value |
| -10.13 | - | - | -27980 | - |
| -10 | -32768 | - | -27648 | - |
| -9 | -29491 | - | -24883 | - |
| -8 | -26214 | - | -22118 | - |
| -7 | -22937 | - | -19354 | - |
| -6 | -19661 | - | -16589 | - |
| -5 | -16384 | - | -13824 | - |
| -4 | -13107 | - | -11059 | - |
| -3 | -9830 | - | -8294 | - |
| -2 | -6554 | - | -5530 | - |
| -1 | -3277 | - | -2765 | - |
| -0.13 | -426 | -384 | -359 | -332 |
| -0.06 | -197 | -197 | -166 | -156 |
| 0 | 0 | 0 | 0 | 0 |
| 1 | 3277 | 3277 | 2765 | 2765 |
| 2 | 6554 | 6554 | 5530 | 5530 |
| 3 | 9830 | 9830 | 8294 | 8294 |
| 4 | 13107 | 13107 | 11059 | 11059 |
| 5 | 16384 | 16384 | 13824 | 13824 |
| 6 | 19661 | 19661 | 16589 | 16589 |
| 7 | 22937 | 22937 | 19354 | 19354 |
| 8 | 26214 | 26214 | 22118 | 22118 |
| 9 | 29491 | 29491 | 24883 | 24883 |
| 10 | 32767 | 32767 | 27648 | 27648 |
| 10.12 | - | - | 27980 | 27980 |
| Code value formula | Code value =(65535/20)*Voltage | Code value =(32767/10)*Voltage | Code value =(55296/20)*Voltage | Code value =(27648/10)*Voltage |
| Voltage formula | Voltage = (Code value*20)/65535 | Voltage = (Code value*10)/32767 | Voltage = (Code value*20)/55296 | Voltage = (Code value*10)/27648 |

Notes: ① When the measuring range of voltage input module is -10V~+10V(-32768~32767), it will support the upper and lower overflow function, that is, when the channel input voltage is more than 10V, the maximum code value of 32767 will be displayed; when the channel input voltage is less than -10V, the minimum code value of -32768 will be displayed.

② When the measuring range of the voltage input module is 0V~10V(0~32767), it will support the functions of lower overflow overshoot, upper and lower overflow and lower overflow alarm. The overshoot means that the channel input range will enter the overshoot when it exceeds the measuring range, and the normal calculation code value will be displayed within the range of -0.13V~+10V. The upper and lower overflow means that when the maximum code value of 32767 will be displayed when the channel input voltage is more than 10V; when the channel input voltage is less than -0.13V, the minimum overshoot code value of -384 will be displayed and an alarm will be given.

③ When the measuring range of voltage input module is -10V~+10V (-27648 ~ 27648), it will support the functions of overshoot, upper and lower overflow and upper and lower overflow alarm. The overshoot means that the channel input range will enter the overshoot when it exceeds the range, and the normal calculation code value will be displayed within the range of -10.13 V ~+10.12 V. The upper and lower overflow means that when the channel input voltage is more than 10.12V, the maximum overshoot code value of 27980 will be displayed and an alarm will be given; when the channel input voltage is less than -10.13V, the minimum overshoot code value of -27980 will be displayed and an alarm will be given.

④ When the range of voltage input module is 0V~10V(0~27648), it will support the functions of overshoot, upper and lower overflow and upper and lower overflow alarm. The overshoot means that the channel input range will enter the overshoot when it exceeds the ranged, and the normal calculation code value will be displayed within the range of -0.13 V ~+10.12 V. The upper and lower overflow means that when the channel input voltage is more than 10.12V, the maximum overshoot code value of 27980 will be displayed and an alarm will be given; when the channel input voltage is less than -0.13V, the minimum overshoot code value of -332 will be displayed and an alarm will be given.

| Measuring range Voltage | -5V~+5V | 0V~5V | 1V~5V |
| --- | --- | --- | --- |
|  | -27648~27648 | 0~27648 | 0~27648 |
|  | Code value | Code value | Code value |
| -5.07 | -27980 | - | - |
| -5 | -27648 | - | - |
| -4 | -22118 | - | - |
| -3 | -16588 | - | - |
| -2 | -11060 | - | - |
| -1 | -5530 | - | - |
| -0.07 | -332 | -332 | - |
| 0 | 0 | 0 | - |
| 0.94 | 5198 | 5198 | -345 |
| 1 | 5530 | 5530 | 0 |
| 2 | 11060 | 11060 | 6912 |
| 3 | 16588 | 16588 | 13824 |
| 4 | 22118 | 22118 | 20736 |
| 5 | 27648 | 27648 | 27648 |
| 5.06 | 27980 | 27980 | 27933 |
| Code value formula | Code value =(55296/10)* Voltage | Code value =(27648/5)*Voltage | Code value =(27648/4)*Voltage -6912 |
| Voltage formula | Voltage = (Code value*10)/55296 | Voltage = (Code value*5)/27648 | Voltage = (Code value +6912)*4/27648 |

Notes: ① When the measuring range of voltage input module is -5V~+5V(-27648~27648), it will support the functions of overshoot, upper and lower overflow and upper and lower overflow alarm. The overshoot means that the channel input voltage will enter the overshoot when it exceeds the range, and the normal calculation code value will be displayed within the range of -5.07V ~+5.06V. The upper and lower overflow means that when the channel input voltage is more than 5.06V, the maximum overshoot code value of 27980 will be displayed and an alarm will be given; when the channel input voltage is less than -5.07V, the minimum overshoot code value of -27980 will be displayed and an alarm will be given.

② When the measuring range of voltage input module is 0V~5V(0~27648), it will support the functions of overshoot, upper and lower overflow and upper and lower overflow alarm. The overshoot means that the channel input range will enter the overshoot when it exceed the range, and the normal calculation code value will be displayed within the range of -0.07 V ~+5.06 V. The overflow means that when the channel input voltage is more than 5.06V, the maximum overshoot code value of 27980 will be displayed and an alarm is given; when the channel input voltage is less than -0.07V, the minimum overshoot code value of -332 will be displayed and an alarm will be given.

③ When the measuring range of voltage input module is 1V~5V(0~27648), it will support the functions of overshoot, upper and lower overflow and upper and lower overflow alarm. The overshoot means that the channel input voltage will enter the overshoot when it exceeds the range, and the normal calculation code value will be displayed within the range of 0.94 V ~ 5.06 V. The overflow means that when the channel input voltage is more than 5.06V, the maximum overshoot code value of 27933 will be displayed and an alarm will be given; when the channel input voltage is less than 0.94V, the minimum overshoot code value of -345 will be displayed and an alarm will be given.

      - Voltage output code value table

| Measuring range Voltage | -10V~+10V | 0V~10V | -10V~+10V | 0V~10V |
| --- | --- | --- | --- | --- |
|  | -32768~32767 | 0~32767 | -27648~27648 | 0~27648 |
|  | Code value | Code value | Code value | Code value |
| -10 | -32768 | - | -27648 | - |
| -9 | -29491 | - | -24883 | - |
| -8 | -26214 | - | -22118 | - |
| -7 | -22937 | - | -19354 | - |
| -6 | -19661 | - | -16589 | - |
| -5 | -16384 | - | -13824 | - |
| -4 | -13107 | - | -11059 | - |
| -3 | -9830 | - | -8294 | - |
| -2 | -6554 | - | -5530 | - |
| -1 | -3277 | - | -2765 | - |
| 0 | 0 | 0 | 0 | 0 |
| 1 | 3277 | 3277 | 2765 | 2765 |
| 2 | 6554 | 6554 | 5530 | 5530 |
| 3 | 9830 | 9830 | 8294 | 8294 |
| 4 | 13107 | 13107 | 11059 | 11059 |
| 5 | 16384 | 16384 | 13824 | 13824 |
| 6 | 19661 | 19661 | 16589 | 16589 |
| 7 | 22937 | 22937 | 19354 | 19354 |
| 8 | 26214 | 26214 | 22118 | 22118 |
| 9 | 29491 | 29491 | 24883 | 24883 |
| 10 | 32767 | 32767 | 27648 | 27648 |
| Code value formula | Code value =(65535/20)*Voltage | Code value =(32767/10)*Voltage | Code value =(55296/20)*Voltage | Code value =(27648/10)*Voltage |
| Voltage formula | Voltage = (Code value*20)/65535 | Voltage = (Code value*10)/32767 | Voltage = (Code value*20)/55296 | Voltage = (Code value*10)/27648 |

Notes: ① The voltage output module supports upper and lower overflow function, that is, when the measuring range of the voltage output module is -10V~+10V or 0V~10V, and the code value is set to be more than the maximum code value corresponding to the range, all channels will output the voltage of 10V;

When the measuring range of the voltage output module is -10V to+10V and the code value is set to be less than the minimum code value corresponding to the range, all channels will output the voltage of -10V;

When the measuring range of the voltage output module is 0V~10V and the code value is set to be less than the minimum code value corresponding to the range, all channels will output the voltage of 0V.

| Measuring range Voltage | -5V~+5V | 0V~5V | 1V~5V |
| --- | --- | --- | --- |
|  | -27648~27648 | 0~27648 | 0~27648 |
|  | Code value | Code value | Code value |
| -5 | -27648 | - | - |
| -4 | -22118 | - | - |
| -3 | -16588 | - | - |
| -2 | -11060 | - | - |
| -1 | -5530 | - | - |
| 0 | 0 | 0 | - |
| 1 | 5530 | 5530 | 0 |
| 2 | 11060 | 11060 | 6912 |
| 3 | 16588 | 16588 | 13824 |
| 4 | 22118 | 22118 | 20736 |
| 5 | 27648 | 27648 | 27648 |
| Code value formula | Code value =(55296/10)*Voltage | Code value =(27648/5)*Voltage | Code value =(27648/4)*Voltage -6912 |
| Voltage formula | Voltage = (Code value*10)/55296 | Voltage = (Code value*5)/27648 | Voltage = (Code value +6912)*4/27648 |

Notes: ① The voltage output module supports the upper and lower overflow function, that is, when the measuring range of the voltage output module is -5V~+5V/0V~5V/1V~5V and the code value is set to be more than the maximum code value corresponding to the range, all channels will output the voltage of 5V;

When the measuring range of the voltage output module is -5V~+5V and the code value is set to be less than the minimum code value corresponding to the range, all channels will output the voltage of -5V;

When the measuring range of the voltage output module is 0V~5V and the code value is set to be less than the minimum code value corresponding to the range, all channels will output the voltage of 0V;

When the measuring range of voltage output module is 1V~5V and the code value is set to be less than the minimum code value corresponding to the range, all channels will output the voltage of 1V.

    - Analog current parameters

      - Current input range selection table

| Current input range selection and code value range |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Range selection | Measuring range | Code value range | Current input calculation formula | Current output calculation formula | Code value correspondence table |
| 0 | Disable, indicating that the channel is not enabled |  |  |  |  |
| 1 | 4mA~20mA | 0~65535 | D=(65535/16)*I-16384 | I=(D+16384)*16/65535 | See Section 3.3.5.3 “Current input code value table” |
| 2 (by default) | 0mA~20mA | 0~65535 | D=(65535/20)*I | I=(D*20)/65535 |  |
| 3 | 4mA~20mA | 0~27648 | D=(27648/16)*I-6912 | I=((D+6912)*16)/27648 |  |
| 4 | 0mA~20mA | 0~27648 | D=(27648/20)*I | I=(D*20)/27648 |  |

Note: D represents code value, I represents current, and the default range of analog current input module is 2: 0mA ~ 20mA (0 ~ 65535).

      - Current output range selection table

| Current output range selection and code value range |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Range selection | Measuring range | Code value range | Current input calculation formula | Current output calculation formula | Code value correspondence table |
| 0 | Disable, indicating that the channel is not enabled |  |  |  |  |
| 1 | 4mA~20mA | 0~65535 | D=(65535/16*I)-16384 | I=(D+16384)*16/65535 | See Section 3.3.5.4 “Current output code value table” |
| 2 (by default) | 0mA~20mA | 0~65535 | D=(65535/20)*I | I=(D*20)/65535 |  |
| 3 | 4mA~20mA | 0~27648 | D=(27648/16)*I-6912 | I=((D+6912)*16)/27648 |  |
| 4 | 0mA~20mA | 0~27648 | D=(27648/20)*I | I=(D*20)/27648 |  |

Note: d represents code value, I represents current, and the default range of analog current output module is 2: 0mA ~ 20mA (0 ~ 65535).

      - Current input code value table

| Measuring range Current | 4mA~20mA | 0mA~20mA | 4mA~20mA | 0mA~20mA |
| --- | --- | --- | --- | --- |
|  | 0~65535 | 0~65535 | 0~27648 | 0~27648 |
|  | Code value | Code value | Code value | Code value |
| 0 | - | 0 | - | 0 |
| 1 | - | 3277 | - | 1382 |
| 2 | - | 6554 | - | 2765 |
| 3 | - | 9830 | - | 4147 |
| 4 | 0 | 13107 | 0 | 5530 |
| 5 | 4096 | 16384 | 1728 | 6912 |
| 6 | 8192 | 19661 | 3456 | 8294 |
| 7 | 12288 | 22937 | 5184 | 9677 |
| 8 | 16384 | 26214 | 6912 | 11059 |
| 9 | 20479 | 29491 | 8640 | 12442 |
| 10 | 24575 | 32768 | 10368 | 13824 |
| 11 | 28671 | 36044 | 12096 | 15206 |
| 12 | 32767 | 39321 | 13824 | 16589 |
| 13 | 36863 | 42598 | 15552 | 17971 |
| 14 | 40959 | 45875 | 17280 | 19354 |
| 15 | 45055 | 49151 | 19008 | 20736 |
| 16 | 49151 | 52428 | 20736 | 22118 |
| 17 | 53247 | 55705 | 22464 | 23501 |
| 18 | 57343 | 58982 | 24192 | 24883 |
| 19 | 61439 | 62258 | 25920 | 26266 |
| 20 | 65535 | 65535 | 27648 | 27648 |
| 20.19 | - | - | 28034 | 27917 |
| 20.24 | - | - | 28085 | 27986 |
| Code value formula | Code value =65535/16*Current-16384 | Code value =(65535/20)*Current | Code value =(27648/16)*Current-6912 | Code value =(27648/20)*Current |

Notes: ① When the measuring range of current input module is 4mA~20mA(0~65535), it will support the functions of upper and lower overflow and upper overflow alarm, that is, when the channel input current is more than 20.03mA, the maximum code value of 65535 will be displayed and an alarm will be given; when the channel input current is less than 4mA, the minimum code value of 0 will be displayed.

(2) When the measuring range of current input module is 0mA~20mA (0~65535), it will support the functions of upper and lower overflow and upper overflow alarm, that is, when the channel input current is more than 20.03mA, the maximum code value of 65535 will be displayed and an alarm will be given; when the channel input current is less than 0mA, the minimum code value of 0 will be displayed.

③ When the measuring range of current input module is 4mA~20mA(0~27648), it will support the functions of upper overflow overshoot, upper and lower overflow and upper overflow alarm. The overshoot means that the channel input current will enter the overshoot when it exceeds the range, and the normal calculation code value will be displayed within the range of 4mA~20.24mA. The upper overflow means that when the channel input current is more than 20.24mA, the maximum overshoot code value of 28085 will be displayed and an alarm will be given. The lower overflow means that when the channel input current is less than 4mA, the minimum overshoot code value of 0 will be displayed.

④ When the measuring range of current input module is 0mA~20mA(0~27648), it will support the functions of upper overflow overshoot, upper and lower overflow and upper overflow alarm. The overshoot means that the channel input current will enter the overshoot when it exceeds the range, and the normal calculation code value will be displayed within the range of 0mA~20.24mA. The upper overflow means that when the channel input current is more than 20.24mA, the maximum overshoot code value of 27986 will be displayed and an alarm will be given. The lower overflow means that when the channel input current is less than 0mA, the minimum overshoot code value of 0 will be displayed.

      - Current output code value table

| Measuring range Current | 4mA~20mA | 0mA~20mA | 4mA~20mA | 0mA~20mA |
| --- | --- | --- | --- | --- |
|  | 0~65535 | 0~65535 | 0~27648 | 0~27648 |
|  | Code value | Code value | Code value | Code value |
| 0 | - | 0 | - | 0 |
| 1 | - | 3277 | - | 1382 |
| 2 | - | 6554 | - | 2765 |
| 3 | - | 9830 | - | 4147 |
| 4 | 0 | 13107 | 0 | 5530 |
| 5 | 4096 | 16384 | 1728 | 6912 |
| 6 | 8192 | 19661 | 3456 | 8294 |
| 7 | 12288 | 22937 | 5184 | 9677 |
| 8 | 16384 | 26214 | 6912 | 11059 |
| 9 | 20479 | 29491 | 8640 | 12442 |
| 10 | 24575 | 32768 | 10368 | 13824 |
| 11 | 28671 | 36044 | 12096 | 15206 |
| 12 | 32767 | 39321 | 13824 | 16589 |
| 13 | 36863 | 42598 | 15552 | 17971 |
| 14 | 40959 | 45875 | 17280 | 19354 |
| 15 | 45055 | 49151 | 19008 | 20736 |
| 16 | 49151 | 52428 | 20736 | 22118 |
| 17 | 53247 | 55705 | 22464 | 23501 |
| 18 | 57343 | 58982 | 24192 | 24883 |
| 19 | 61439 | 62258 | 25920 | 26266 |
| 20 | 65535 | 65535 | 27648 | 27648 |
| 22.81 | - | - | 32511 | 31538 |
| 23.52 | - | - | - | 32511 |
| Code value formula | Code value =65535/16*Current-16384 | Code value =(65535/20)*Current | Code value =(27648/16)*Current-6912 | Code value =(27648/20)*Current |

Note: ① When the measuring range of current output module is 4mA~20mA(0~27648) and 0mA~20mA(0~27648), it will supports the functions of upper overflow overshoot, upper overflow and upper overflow alarm, that is, when the measuring range of current output module is 4mA~20mA(0~27648) and the code value is set to be more than 32511, all channels will output the current of 22.81mA and give an alarm; when the measuring range of current output module is 0mA~20mA (0~27648) and the code value is set to be more than 32511, all channels will output the current of 23.52mA and give an alarm.

    - Wiring diagram

      - SRR3214

*COM internal conduction, PE internal conduction

* Shielded twisted pair is recommended for signal cables

      - SRR3234

*COM internal conduction, PE internal conduction

* Shielded twisted pair is recommended for signal cables

      - SRR4014

*COM internal conduction, PE internal conduction

* Shielded twisted pair is recommended for signal cables

      - SRR4034

*COM internal conduction, PE internal conduction

* Shielded twisted pair is recommended for signal cables

    - Overall dimension drawing

Dimensions of analog I/O terminal (mm)

  - Terminal cover

    - Overall dimension drawing

Dimensions of terminal cover (mm)

Note: DIN 35 mm standard guide rails are used for installation, with the dimensions of 35*7.5*1.0 and 35*15*1.0 (mm).

- Installation and Removal

  - Installation guide

Precautions for installation\removal

- The protection level of the module is IP20. The module shall be installed in the cabinet for indoor use.

- The cabinet shall be provided with good ventilation measures (such as, an exhaust fan).

- Do not install this device next to or above the device that may cause overheating.

- Must install the module vertically on the fixed guide rail and keep the surrounding air circulation (there shall be at least 50mm space above and below the module for air circulation).

- Carry out the installation\removal when the power supply is cut off.

- After the module is installed, the wiring shall be carried out below and above the device.

Caution

- If the device is not used in accordance with the user manual, the protection provided may be damaged.

Ensure that the module is installed vertically on the fixed guide rail.

  - Installation and removal steps

| Module installation and removal |  |
| --- | --- |
| Installation steps | 1. Install the coupler module on the fixed guide rail. |
|  | 2. Install the required I/O terminals or functional modules on the right side of the coupler module in turn. |
|  | 3. Install the terminal cover to complete the module assembly. |
| Removal steps | 1. Open the module buckle with a flat screwdriver. |
|  | 2. Pull out the module to be removed. |

  - Installation/removal schematic diagram

Installation of the coupler module

- Align the coupler module vertically with the guide rail slot, as shown in Fig. ① below.

- Press the coupler module toward the guide rail; when you hear a “Click” sound, the module will be installed in place, as shown in Fig. ② below.

- Push the buckle in the direction of the guide rail; when your hear a “Click” sound, the module is installed in place, as shown in Fig. ③ below.

Installation of I/O terminal

- Install the required I/O terminals or functional modules one by one according to the above steps for installing the coupler module, and push them in place as shown in the Figs. ④, ⑤ and ⑥; when you hear a “Click” sound, the modules are installed in place.

④

⑤

⑥

Installation of the terminal cover

- Install the terminal cover on the right side of the last module, and align the slot side of the terminal cover with the guide rail. For the installation method, please refer to the installation method of I/O terminals; push the terminal cover into place, as shown in Fig. ⑦ below.

⑦

- After the terminal cover is installed, check whether the front of the whole module is smooth, and ensure that all modules and end cover are installed in place and the front is flush, as shown in Fig. ⑧ below.

⑧

Removal

- Insert the flat screwdriver into the buckle of the module to be removed, and apply a force (hear noise) in the direction of the module, as shown in Fig, ⑨ below.

⑨

- Remove the module in the reverse operation of installing the module, as shown in the Fig. ⑩ below.

⑩

- Wiring

  - Wiring terminal

Caution

| Wiring terminal |  |  |
| --- | --- | --- |
| Power terminal | Rated voltage | 250V |
|  | Rated current | 8A |
|  | Number of pins | 6P |
|  | Wire diameter | 24~16 AWG 0.2~1.5 mm² |
| Signal line terminals (input and output terminals) | Rated voltage | 150V |
|  | Rated current | 8A |
|  | Number of pins | 18P |
|  | Wire diameter | 28~16 AWG 0.2~1.5 mm² |
| Fieldbus ports | 2×RJ45 | Category 5 or above UTP or STP port (STP ports recommended) |

  - Wiring instructions and requirements

Precautions on the power wiring

- The power supplies on the module system side and the field side shall be configured and used separately; do not mix them.

- PE shall be grounded reliably.

Wiring tool requirements

The power terminal and signal line terminal are designed without screws, and all wires can be installed and removed with a flat screwdriver (with a size of ≤3mm).

Wire stripping length requirements

The recommended wire stripping length for power and signal line terminals is 10 mm.

Wiring methods

The single-stranded hard wires shall be stripped to the corresponding length, and directly inserted into the corresponding terminal holes by pressing the button.

The multi-strand flexible wires shall be stripped to the corresponding length, directly connected or matched with cold-pressed terminals (for reference sizes of tubular insulation terminals, please see the following table) and then insulated directly into the corresponding end holes by pressing the button.

The sizes of power terminals and signal line terminals are shown in the following table:

| Tubular insulation terminal size table |  |  |
| --- | --- | --- |
| Size requirements | Model | Wire cross-sectional area (mm2) |
| The length L of the tubular insulated terminal is 10mm. | E0310 | 0.3 |
|  | E0510 | 0.5 |
|  | E7510 | 0.75 |
|  | E1010 | 1.0 |
|  | E1510 | 1.5 |

Caution

- Only copper wires can be used for wiring conductors.

Caution

- The cable temperature shall be 80℃.

- Usages

  - Description of parameters

    - Digital input filtering

The digital input filtering is used to prevent unexpected rapid changes in the program response input signal, which may be caused by switch contact jumping or electrical noise. The digital input filtering supports single module setting, each module can be configured separately, but the channels cannot be configured separately.

At present, the default digital input FilterTime is 3ms, and the supported setting ranges are no filtering, 0.1ms, 0.2ms, 0.5ms, 1ms, 2ms, 3ms (factory setting), 4ms...18ms, 19ms and 20ms. When it is 3ms, the stray waves within 3ms can be filtered. The input filtering time of 3ms means that a single signal changes from "0" to "1" or from "1" to "0" for 3ms before it can be detected, while a single high pulse or low pulse shorter than 3ms will not be detected.

Function description: When the input filtering time is 1ms, the stray waves within 1ms can be filtered. As shown below, when a signal of 250us is input, it will be regarded as an invalid signal, and a single high pulse or low pulse shorter than 1ms will not be detected, while the signals longer than 1ms can be collected.

1ms

Valid signal

Output signal

Invalid signal 250us

Input signal

    - Digital output signal clearing/holding

The clearing/holding function is used for modules with output channels. This function can be configured for the output mode of the output channels when the module is in non-OP state (when the operation stops or the coupler network cable is disconnected). This parameter supports the following output states:

Clear the output: When the communication is disconnected, the output will be automatically cleared in the module output channel, that is, output 0.

Output a valid value: When communication is disconnected, the valid value will be output in the module output channel, that is, output 1.

Hold the last output value: when the communication is disconnected, the last output value will be held in the module output channel.

The digital clearing and holding function supports the overall setting of the module (template mode) and the single channel setting (single channel mode). Any channel can be set in single channel mode or template mode, and the single channel mode has higher priority than the template mode. The specific configuration method is shown in the following table. By default, the output will be cleared as a whole.

| Clearing/holding parameters of digital output module |  |  |  |  |
| --- | --- | --- | --- | --- |
| Parameter name | Parameter meaning | Parameter value | Parameter value meaning | Default value |
| Template Mode | Template mode | 1 | Preset Low: Clear the output, that is, output 0 | 1 |
|  |  | 2 | Preset High: Output a valid value, that is, output 1 |  |
|  |  | 3 | Keep Mode: Hold the last output value |  |
| Channel x | Single channel mode | 0 | Template Value: Template mode value, that is, the single channel mode is not enabled | 0 |
|  |  | 1 | Preset Low: Clear the output, that is, output 0 |  |
|  |  | 2 | Preset High: Output a valid value, that is, output 1 |  |
|  |  | 3 | Keep Mode: Hold the last output value |  |

    - Analog range setting

The analog range setting Range Select is used to set the measuring range of analog, and each channel can be configured separately (see Sections 3.3.4 and 3.3.5 “Analog parameters” for the range).

    - Analog input filtering

- Analog input filtering function

The analog input filter is used to average the data after A/D conversion internally, to reduce the fluctuation influence of the input signal caused by the noise.

The analog input is moved and averaged with specified A/D conversion times.

- Filtering function configuration

Each channel can be configured separately, ranging from 1 ~ 200, with a default of 10 times.

    - Analog output signal clearing/holding

The clearing/holding function is used for modules with output channels. This function can be configured for the output mode of the output channels when the module is in non-OP state (when the operation stops or the coupler network cable is disconnected). This parameter supports the following output states:

Clear the output: When the communication is disconnected, the output will be automatically cleared in the module output channel.

Hold the output: When communication is disconnected, the output will be held in the module output channel.

Output a preset value: when the communication is disconnected, the preset value will be output in the module output channel.

The analog clearing and holding function supports the overall setting (template mode) and the single channel setting (single channel mode) of the module. Any channel can be set in single channel mode or template mode, and the single channel mode has higher priority than the template mode. The specific configuration method is shown in the following table. By default, the output will be cleared as a whole

| Clearing/holding parameters of analog output module |  |  |  |  |
| --- | --- | --- | --- | --- |
| Parameter name | Parameter meaning | Parameter value | Parameter value meaning | Default value |
| TemplateMode | Template mode | 0 | Clear: Clear the outputs in all channels | 0 |
|  |  | 1 | Hold: Hold the output in all channels |  |
|  |  | 2 | Preset: Output the preset value in all channels |  |
| TemplateValue Chx | Single channel clearing/holding mode | 0 | TemplateValue: Template mode value, that is, single channel mode is not enabled | 0 |
|  |  | 1 | Clear: Clear the output in the single channel |  |
|  |  | 2 | Hold: Hold the output in the single channel |  |
|  |  | 3 | Preset: Output the preset value in the single channel |  |
| Preset Value Chx | Setting of the preset value in single channel | Code value range | Output the current/voltage value corresponding to code value (corresponding to the range code value table) | 0 |

Note: When the overall setting of the module (template mode) is set to 2, that is, the preset values output in all channels are valid, the preset value shall be based on that of Channel 0 in the single-channel preset values, and the all-channel output will be performed.

    - Analog value power-off preservation

The analog parameters support the function of saving all configuration parameters of the module when communication is disconnected due to abnormal power failure, and the analog modules support the power failure saving function by default.

In this user manual, the parameter configuration method of the combination of SRR8200 couplers +I/O terminals is introduced with Sysmac Studio as an example. For specific steps, please see Section 6.3.1 “Parameter settings”. After modification, it is recommended to power on the device again.

  - Fault code information

    - General fault codes of coupler

| Type | No. | Error type | Error code | Event name | Event code (2#) | Event code (10 #) | Event code (16 #) | troubleshooting |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| General errors | 2 | Online upgrade error | 1 | The firmware upgrade is abnormal | 0000000010000001 | 129 | 0x0081 | Upgrade it again, and check whether there is interference in the environment and whether the firmware is too large |
|  |  |  | 2 | The firmware does not match the current module model | 0000000010000010 | 130 | 0x0082 | Check whether the file is correct, and whether there is abnormality or interference in the module |
|  | 3 | Voltage error | 5 | The voltage on the load side is not applied | 0000000011000101 | 197 | 0x00C5 | Check whether the power supply on the field side is connected |
|  | 6 | Channel error | 4 | There is channel upper or lower overflow | 0000000110000100 | 388 | 0x0184 | Check whether the input signal of the corresponding channel is beyond the measuring range and whether the output signal is beyond the configurable range |
|  | 7 | Parameter error | 0 | The parameter setting is abnormal | 0000000111000000 | 448 | 0x01C0 | Check the module parameter setting |
|  | 63 | Communication error | 1 | The initialization fails | 0000111111000001 | 4033 | 0x0FC1 | Check whether the module is connected normally |
|  |  |  | 2 | The token is timeout | 0000111111000010 | 4034 | 0x0FC2 | Check whether there is abnormality or interference in the module |
|  |  |  | 3 | The module runs offline | 0000111111000011 | 4035 | 0x0FC3 | Check whether the module is online or there is interference |
|  |  |  | 4 | The parsing data CRC is error | 0000111111000100 | 4036 | 0x0FC4 | Check whether there is abnormality or interference in the module |

    - Viewing fault codes

With TwinCAT3 software as an example, view the alarm information under “Error” in the “Error List” window, as shown below. The alarm code is Hex: 00c5, which means that the voltage is error, and the voltage on the load side is not applied. You can check whether the power supply on the field side is connected.

The event information viewing method is shown in the following table:

| Structure of event information |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| byte0 | byte1 | byte2 | byte3 | byte4 | byte5 | byte6 | byte7 |
| Event code |  | Event status | Module station number | Product line |  | Channel number |  |
|  |  | For example: 0x01: Event generated 0x00: Event disappeared |  |  |  | For example: 0xFF: Channel level event. 0x00: Channel 0 |  |

  - Configuration application of EtherCAT coupler

    - Application in Sysmac Studio software environment

- Preparation

- Hardware environment

- Module preparation, with SRR8200+SRR1016+SRR2116+SRR3214+SRR4034 topology as an example

- 1 computer, with Sysmac Studio software pre-installed

- 1 Omron PLC, with NJ301-1100 as an example

- EtherCAT special shielded cable

- 1 switching power supply

- Device configuration file

Please contact our company`s staff for the configuration file.

- Hardware configuration and wiring

Please follow the requirements of Section 4 “Installation and removal” and Section 5 “Wiring”.

- Computer IP requirements

Set the IP address of the computer and the IP address of the PLC to ensure that they are in the same network segment.

- Create a new project

Open Sysmac Studio software and click “Create a New Project”.

- Project Name: user-defined.

- Select Device: Select the corresponding PLC model, and the corresponding PLC version number.

Click “Create” after entering the project attributes.

Click “Controller-> Communication Settings" in the menu bar, select the method for connecting with the controller every time online, and enter the "Remote IP Address", as shown below.

Click "Ethernet Communication Test". The system will display that the test is successful.

- Install the XML file

Expand “Configuration and Settings” in the navigation tree on the left and double-click “EtherCAT”.

Right-click "Master Device" and select "Display ESI Library", as shown below.

Click “Install (File)” in the pop-up “ESI Library” window, select the XML file path of the module, and click “Yes” to complete the installation, as shown below.

- Add a device

There are two ways to add devices: Online scanning and offline adding, which is described with the offline adding as an example.

Under the "Toolbox" bar on the right, click to expand all suppliers and select "SINSEGYE", as shown below.

Click to select “SRR Series Fieldbus”, and double-click “SRR8200 Coupler Module” to add a slave device, as shown below.

On the “EtherCAT” main interface, select the newly added SRR8200 coupler module and select “Edit Module Configuration”, as shown below.

Locate the cursor in "Module", click “Module” in the list of modules of the toolbox on the right, and add I/O terminals one by one in the order of I/O terminal configuration.

Note: The order and model must be consistent with the physical topology.

- Set the node address

Click "Controller-> Online" in the menu bar to turn the controller to online status. Right-click the “Master Device” and click to select "Write Slave Device Node Address", as shown below.

- In the window of setting node address, click the numerical value under the setting value, enter the node address, and click "Write" to change the slave device node address, as shown below.

After writing, a power-on prompt will pop up, as shown below, click "Write", and then restart the power supply of the slave device according to the prompt.

- PLC Download the configuration to PLC

Click the "Controller-> Transmitting (A)-> Transmitting to Controller (T)" button in the menu bar, as shown below.

Download the configuration to PLC. The transmission confirmation window will pop up. Click "Execute", and click "Yes/OK" in the subsequent pop-up windows in turn, as shown below. After downloading, please power on the device again.

- Parameter settings

Switch the configuration to offline state, edit the module configuration interface of Node 1, select the SRR1016 module, and click “Edit Initialization Parameter Settings”, as shown below.

Note: If the firmware version of PLC is too low, please write and read SDO address with EC_CoESDOWrite and EC_CoESDORead instructions.

On the parameter setting interface of SRR1016, configure the digital input filtering function, as shown below.

Set the digital input FilterTime within the range of 0 ~ 20 ms. After configuration, click "Apply" and "OK", as shown below. After all the parameters are configured, download the program to the PLC again, and the PLC and power on the module again.

Edit the module configuration interface of Node 1, select the SRR2116 module and click “Edit Initialization Parameter Settings”, as shown below.

On the parameter setting interface of SRR2116, configure the function of clearing/holding the digital output signal, as shown below.

For clearing/holding function of digital output signal, by default, all channels are preset as output clearing mode, and the module channels can be configured separately. See Section 6.1.2 Digital output signal clearing/holding for the correspondence relationship. After configuration, click "Apply" and "OK", as shown below. After all the parameters are configured, download the program to the PLC, and power on the PLC and the module again.

Edit the module configuration interface of Node 1, select the SRR3214 module and click “Edit Initialization Parameter Settings”, as shown below.

On the parameter setting interface of SRR3214 analog voltage input module, configure the analog voltage range and analog input filter parameters, as shown below.

The analog input voltage can be configured within 8 measuring ranges, and each channel can be configured separately. After configuration, click "Apply" and "OK", as shown below. After all the parameters are configured, download the program to the PLC, and power on the PLC and the module again.

The analog input filter can be configured within the range of 1~200, which supports single-channel independent configuration. After configuration, click "Apply" and "OK", as shown below. After all the parameters are configured, download the program to the PLC, and power on the PLC and the module again.

Edit the module configuration interface of Node 1, select the SRR4034 module and click "Edit Initialization Parameter Settings", as shown below.

On the parameter setting interface of SRR4034 analog current output module, configure the analog current range and the analog output signal clearing/holding parameters, as shown below.

The analog output current can be configured within 5 measuring ranges, and each channel can be configured separately. After configuration, click "Apply" and "OK", as shown below. After all the parameters are configured, download the program to the PLC, and power on the PLC and the module again.

For the analog output signal clearing/holding function, by default, all channels are in output clearing mode, and the module channels can be configured separately. See 6.1.5 “Analog output signal clearing/holding for the correspondence relationship. After configuration, click "Apply" and "OK", as shown below. After all the parameters are configured, download the program to the PLC, and power on the PLC and the module again.

- I/O functions

Double-click "I/O Mapping" in the navigation tree on the left to see the mapping table of each module in the topology, so as to monitor the input and output values of each channel of each module, as shown below.

Expand the mapping table of SRR1016 digital quantity module. When a valid voltage is input in the input channel, the input value can be monitored in the mapping table, as shown below.

Expand the mapping table of SRR2116 digital module, and the output can be controlled in the output channel by modifying the channel value, as shown below.

Expand the mapping table of SRR3214 analog module and monitor the input voltage code value of each channel, as shown below. See Sections 3.3.4 and 3.3.5 “Analog parameters” for the correspondence relationship between code values and voltages.

Expand the mapping table of SRR4034 analog module, and write the current code value to force the output in each channel, as shown below. See Sections 3.3.4 and 3.3.5 “Analog parameters” for the correspondence relationship between code values and currents.

  - Online upgrade of firmware

Take TwinCAT3 software as an example, with the topology of SRR8200+SRR2216, as shown below.

Click the coupler "SRR8200" in the navigation tree on the left, click the "Online" option in the right menu, click the "Bootstrap" option in the State Machine, and then click the "Download" option in the File Access over EtherCAT below after the "BOOT" status is displayed in the Current State, as shown below.

Open the file window, select the "All Files" option, select the bin file corresponding to the module to be upgraded, and click "Open", as shown below.

Pop up the setting window, enter “Password”, where the password “0” means upgrading the coupler, and click “OK” to upgrade it, as shown below. Note: To upgrade the corresponding slave module, must enter the corresponding station number in “Password”, for example, to upgrade SRR2216, please enter 1. After confirming the upgrade, observe the progress bar and module performance below to check whether the upgrade is successful (see the next step for details).

- Successful upgrading process of different modules

Online upgrade of EtherCAT coupler:

After the progress bar is full, the coupler IOR will flash at 10Hz (with a cycle of 50ms On and 50ms Off);

When IOR flashes at the frequency from 10Hz to 1Hz, it indicates that the upgrade is successful;

After the online upgrade is successful, must manually switch it to the OP state before re-establishing the connection;

If repeated upgrade is required, please switch the OP state to the BOOT state again.

IOOnline upgrade of IO terminal:

After the progress bar is full, the coupler IOR and the RUN of the module to be upgraded will flash at 10Hz (with a cycle of 50ms On and 50ms Off);

- The RUN of the module to be upgraded flashes at the frequency from 10Hz to Off, it indicate that the upgrade is successful (power on and off the module again for normal connection after the upgrade is completed);

You can continue to upgrade other modules without power-off.