Manual for SRE Series Products

Ver 1.7

Content

1. Product Model	9

2. SRE8200	10

2.1 Electrical Specifications	10

2.2. Wiring Diagram	11

2.3 Terminal Description	12

2.4. Indicator Description	12

3. SRE9020	13

3.1 Electrical specifications	13

3.2. Wiring Diagram	14

3.3. Module Description	15

4. Digital Input Module	16

4.1. Electrical Specifications	16

4.2. Wiring Diagram	17

4.2.1. SRE1016 Wiring Diagram	17

4.2.2. SRE1032 Wiring Diagram	18

4.3. Interface Description	19

4.3.1. SRE1016 Indicator Description	19

4.3.2. SRE1032 Indicator Description	19

4.4. Indicator Description	19

4.4.1. SRE1016 Indicator Description	19

4.4.2 SRE1032 Indicator Description	19

4.5. COE General Parameter Description	20

5. Digital Output Module	21

5.1. 16 Point Digital Output Electrical Specifications	21

5.2. 32 Point Digital Output Electrical Specifications	22

5.3. Wiring Diagram	23

5.3.1. SRE2116 Wiring Diagram	23

5.3.2. SRE2216 Wiring Diagram	24

5.3.3. SRE2132 Wiring Diagram	25

5.3.4. SRE2232 Wiring Diagram	26

5.4. Indicator Description	27

5.4.1. SRE2216/SRE2116 Indicator Description	27

5.4.2. SRE2232/SRE2132 Indicator Description	27

5.5. COE General Parameter Description	28

6. Digital Fast Output Module	29

6.1. Electrical Specifications	29

6.2. Wiring Diagram	30

6.2.1. SRE5202 Wiring Diagram	30

6.2.2. SRE5204 Wiring Diagram	31

6.3. Terminal Description	32

6.3.1. SRE5202 Terminal Description	32

6.3.2. SRE5204 Terminal Description	32

6.4. Indicator Description	32

6.4.1. SRE5202 Indicator Description	32

6.4.2. SRE5204 Indicator Description	32

6.5. Parameter Description	34

6.5.1. COE Parameter Description	34

6.5.2. DC/Oversampling Parameter Description	35

6.5.3. Codesys/Distributed Clocks	36

7. Digital Input/Output Module	37

7.1. Electrical Specifications	37

7.2. Wiring Diagram	39

7.2.1. SRE1332 Wiring Diagram	39

7.2.2. SRE1432 Wiring Diagram	40

7.3. Indicator Description	41

7.4. COE General Parameter Description	41

8. Analog Rapid Acquisition Input Module	43

8.1. Electrical Specifications	43

8.2. SRE3522 Module Wiring Diagram	44

8.3. Indicator Description	45

8.4. Terminal Description	45

8.5. Parameter Description	45

9. Analog Input Module	46

9.1. Electrical Specifications	46

9.2. Module Wiring Diagram	47

9.2.1. SRE3204 Wiring Diagram	47

9.2.2. SRE3208 Wiring Diagram	48

9.3. Terminal Description	49

9.3.1. SRE3204 Terminal Description	49

9.3.2. SRE3208 Terminal Description	49

9.4. Indicator Description	49

9.5. COE General Parameter Description	49

10. Analog Output Module	50

10.1. Electrical Specifications	50

10.2. Module Wiring Diagram	52

10.2.1. SRE4204 Wiring Diagram	52

10.2.2. SRE4208 Wiring Diagram	53

10.3. Indicator Description	54

10.4. Terminal Description	54

10.4.1. SRE4204 Terminal Description	54

10.4.2. SRE4208 Terminal Description	54

10.5. COE General Parameter Description	55

11. Temperature Measurement Module	56

11.1. Thermocouple Measurement Module SRE3284	56

11.1.1. Electrical Specifications	56

11.1.2. Module Wiring Diagram	57

11.1.3. Terminal Description	58

11.1.4. Indicator Description	58

11.1.5. COE Parameter Description	59

11.2. Thermal Resistance Measurement Module SRE3274	60

11.2.1. Electrical Specifications	60

11.2.2. Module Wiring Diagram	61

11.2.3. Terminal Description	62

11.2.4. Indicator Description	62

11.2.5. COE Parameter Description	63

12. Power Relay Module SRE9001	64

12.1. Electrical Specifications	64

12.2. Module Wiring Diagram	65

12.3. Indicator Description	66

12.4. Terminal Description	66

13. Serial Port Module	66

13.1. Electrical Specifications	67

13.2. Module Wiring Diagram	68

13.2.1. SRE6002 Wiring Diagram	68

13.2.2. SRE6004 Wiring Diagram	69

13.3. Indicator Description	70

13.3.1. SRE6002 Indicator Description	70

13.3.2. SRE6004 Indicator Description	70

13.4. Module Terminal Description	71

13.4.1. SRE6002 Terminal Description	71

13.4.2. SRE6004 Terminal Description	72

13.5. Parameter Description	73

13.5.1. COE General Parameter Description	73

13.5.2. Parameter Description	74

13.6. Configuration Module Description	75

13.6.1. Modbus Master Configuration	75

13.6.2. Modbus Slave Configuration	77

13.6.3. Free Port Configuration	78

14. High-speed Counting Module	81

14.1. Electrical Specifications	81

14.2. Wiring Diagram	82

14.2.1. SRE5012 Wiring Diagram	82

14.2.2. SRE5034 Wiring Diagram	83

14.3. Indicator Description	84

14.3.1. SRE5012 Indicator Description	84

14.3.2. SRE5034 Indicator Description	85

14.4. Module Terminal Description	86

14.4.1. SRE5012 Terminal Description	86

14.4.2. SRE5034 Terminal Description	87

14.5. RXPDO Parameter Description	88

14.6. TXPDO Parameter Description	89

14.7. Parameter Configuration Instructions (Channels)	90

14.7.1. SRE5012	90

14.7.2. SRE5034	91

14.8. Parameter Configuration Description (Latch)	92

14.8.1. SRE5012	92

14.8.2. SRE5034	92

14.9. Gated Output Mode Description	94

14.9.1. Gated Output Mode 1	94

14.9.2. Gated Output Mode 2	95

14.9.3. Gated Output Mode 3	96

14.9.4. Gated Output Mode 4	97

15. High-speed pulse output module SRE5234	98

15.1. Electrical Specifications	98

15.2. Electrical Wiring Diagram	99

15.3. Indicator Description	100

15.4. Indicator Description	101

15.5. COE Parameter Description	102

15.6. PDO Parameter Description	103

16. Usage Example	105

16.1. SRE8200 Coupler and Communication Instructions with BECKHOFF Main Station	105

16.1.1. Communication Connection	105

16.1.2. Hardware Configuration	105

16.1.3. Install XML Files	106

16.1.4. New Project and Configuration	106

16.1.5. Data Monitoring	108

16.2. Example of Communication between SRE2116 and TwinCAT3	109

16.2.1. Communication Connection	109

16.2.2. Hardware Configuration	109

16.2.3. Install XML Files	110

16.2.4. New Project and Configuration	110

16.2.5. Data Monitoring	111

16.3. SRE3204 Communication Example	112

16.3.1. Example of Communication with TwinCAT3	112

16.3.2. Example of Communication with Omron	115

16.4. Example of Communication between SRE3522 and TwinCAT3	121

16.4.1. Communication Connection	121

16.4.2. Hardware Configuration	121

16.4.3. Install XML Files	122

16.4.4. New Project and Configuration	122

16.4.5. Data Monitoring	124

16.5. Example of Communication between SRE6004 and TwinCAT3	125

16.5.1. Communication Connection	125

16.5.2. Hardware Configuration	125

16.5.3. Install XML Files	126

16.5.4. New Project and Configuration	126

16.5.5. Modbus RTU Communication of SRE6004	128

16.5.6. SRE6004 Free Port Communication	134

16.5.7. SRE6004 as Modbus Slave	138

16.6. Example of Communication between SRE5034 and TwinCAT3	140

16.6.1. Communication Connection	140

16.6.2. Hardware Configuration	141

16.6.3. Install XML Files	141

16.6.4. New Project and Configuration	141

16.6.5. Data Monitoring	143

16.7. Example of Communication between SRE5202 and TwinCAT3	144

16.7.1. Communication Connection	144

16.7.2. Hardware Configuration	144

16.7.3. Install XML Files	145

16.7.4. New Project and Configuration	145

16.7.5. Data Monitoring	147

16.8. Example of Communication between SRE5234 and TwinCAT3	149

16.8.1. Communication Connection	149

16.8.2. Hardware Configuration	149

16.8.3. Install XML Files	150

16.8.4. New Project and Configuration	150

16.8.5. Data Monitoring	152

Appendix Configuration Parameter Description	153

TwinCAT3 Startup Function Description	153

Codesys Startup Parameter Setting Extension Module Parameter Description	156

Description of Sysmac Studio Initialization Parameter Setting Function	157

| Manual version | Description |
| --- | --- |
| V1.0 | Initial version. |
| V1.1 | Update product, add product description of SRE1032, SRE2322, SRE2132, SRE1332, SRE1432, SRE3208, and SRE4208 |
| V1.2 | Add product description of SRE3522 |
| V1.3 | Add product description of SRE3274 and SRE3284 |
| V1.4 | Add product description of SRE9001, SRE6002, SRE6004, SRE5012, SRE5034, SRE5202, SRE5204 and SRE9020 |
| V1.5 | Add product description of SRE5234 |
| V1.6 | Update SRE5234 PDO parameters and SRE5012 gate parameters. |
| V1.7 | Update SRE5012 parameter configuration |

- Product Model

SRE series products are high-performance EtherCAT modules, including couplers, digital input/output modules, analog input/output modules, temperature measurement modules, etc. They are powered by 24VDC and equipped with a module diagnostic function. The product list is as follows:

| Model | Description |
| --- | --- |
| SRE8200 | EtherCAT bus, 2 RJ45 ports, high-performance backplane bus, and it can expand up to 64 modules at most. |
| SRE9020 | -- |
| SRE1016 | 16-channel digital input, supporting PNP/NPN input. |
| SRE1032 | 32-channel digital input, supporting PNP/NPN input. |
| SRE1332 | 16-channel NPN input, 16-channel transistor NPN type output. |
| SRE1432 | 16-channel PNP input, 16-channel transistor PNP type output. |
| SRE2116 | 16-channel digital output, with NPN transistors, rated at 0VDC (±3V)/0.5A. |
| SRE2216 | 16-channel digital output, with PNP transistors, rated at 24VDC/0.5A. |
| SRE2132 | 32-channel digital output, with NPN transistors, rated at 0VDC (±3V)/0.5A, and the total current of a single module does not exceed 10A. |
| SRE2232 | 32-channel digital output, with PNP transistors, rated at 24VDC/0.5A, and the total current of a single module does not exceed 10A. |
| SRE3522 | Two-channel analog fast acquisition module |
| SRE3204 | 4-channel voltage/current input, with a precision of 16 bits. |
| SRE3208 | 8-channel voltage/current input, with a precision of 16 bits. |
| SRE3284 | 4-channel thermocouple input module. |
| SRE3274 | 4-channel thermal resistance input module. |
| SRE4204 | 4-channel voltage/current output, ±10V or 0~20mA, with a precision of 16 bits. |
| SRE4208 | 8-channel voltage/current output, ±10V or 0~20mA, with a precision of 16 bits. |
| SRE5012 | 2-channel high-speed counting module, with 2 groups of A, B, C counting inputs, single-ended (rated at 24V, maximum 200KHZ, supporting PNP/NPN input) or differential (5V, maximum 4MHZ), and supporting ordinary counting function. |
| SRE5034 | 4-channel high-speed counting module, with 4 groups of A, B, C counting inputs, differential (5V, maximum 4MHZ), and supporting ordinary counting function. |
| SRE5234 | High-speed pulse output module, 4-axis PTO output, NPN type single-ended output max. 400KHZ (at 5V), differential output max. 1MHZ. |
| SRE6002 | Serial port module, with 2 RS422/RS232/RS485 interfaces, supporting Modbus RTU and free port protocols, and the maximum baud rate is 115.2Kbps. |
| SRE6004 | Serial port module, with 4 RS422/RS232/RS485 interfaces, supporting Modbus RTU and free port protocols, and the maximum baud rate is 115.2Kbps. |
| SRE9001 | Power relay module |

- SRE8200

  - 2.1 Electrical Specifications

| Model | SRE8200 module |
| --- | --- |
| Product overview | 2 RJ45 interfaces, stable 24VDC power supply performance, strong anti-interference performance |
| Technical specifications |  |
| Order No. | SRE8200 |
| Electrical interface | RJ45 |
| Working power supply | 18~28V DC |
| Is the CPU connected? | No (independent slave) |
| Support agreement | EtherCAT Slave |
| Quantity of built-in IO | None |
| Station setting |  |
| Address setting | Configure by dip switch or main station |
| Maximum quantity of stations per segment | 255 |
| Isolation |  |
| Between channel and bus | Yes |
| Power supply to bus | Yes |
| Display indication | Power supply+24V green light, BF red light, RUN red light |
| System power diagnosis and warning | Support |
| Operating environment | Operating temperature: -10 ～ 55 °C; Relative humidity: 5% to 90% (no condensation) |
| Dimensions (length x width x height) | 48×80×100mm |

  - 2.2. Wiring Diagram

Figure 1-2

Note: Us is the power terminal of the coupler, and Up is the power terminal of the expansion module.

  - 2.3 Terminal Description

| Wiring terminals | Description |
| --- | --- |
| Up_24V | Positive electrode of coupler power supply terminal |
| Up_0V | Negative electrode of coupler power supply terminal |
| Us_24V | Positive electrode of expansion module power supply terminal |
| Us_0V | Negative electrode of expansion module power supply terminal |

  - 2.4. Indicator Description

| Indicator | Description |
| --- | --- |
| PWR (Green) | Coupler power indicator: On: module power supply is normal; Off: The module is not powered or its power supply is abnormal. |
| PWR_IO (Green) | IO power indicator: On: IO power supply is normal Off: IO is not powered or its power supply is abnormal |
| BF (Red) | Bus fault indicator: Remain ON: Configuration error Off: The module functions properly |
| RUN (Yellow) | Bus communication indicator: Flashing: Module is normal OFF: Communication malfunction |

- SRE9020

  - 3.1 Electrical specifications

| Model | SRE9020 |
| --- | --- |
| Product overview | 1 RJ45 interface |
| Technical specifications |  |
| Ordering number | SRE9020 |
| Electrical interface | RJ45 |
| Power supply | 18~28V DC |
| Supported protocols | EtherCAT slave station |
| Number of built-in IO on the main body | None |
| Isolation |  |
| Between channel and bus | Yes |
| Power supply to the bus | Yes |
| Display indicators | Power and RUN green indicator lights |
| System power supply diagnosis and warning | Support |
| Operating environment | Operating temperature: - 10~55℃; Relative humidity: 5%~90% (no condensation) |
| Dimensions (length x width x height) | 24×100×80 (mm) |

  - 3.2. Wiring Diagram

  - 3.3. Module Description

The network port OUT of the module is used for EtherCAT communication. It should be connected to the IN port of the next-level EtherCAT slave station. When SRE9020 is applied, it needs to be connected to the last module in the combination.

The ECT couplers connected through OUT port of SRE9020

The expansion modules connected to SRE8200 coupler

- Digital Input Module

High performance digital input module, 16/32 digital input, NPN/PNP input, 24VDC, with module diagnostic function.

  - Electrical Specifications

| Model | SRE1016 | SRE1032 |
| --- | --- | --- |
| Technical specifications |  |  |
| Input points | 16 | 32 |
| Bus 5VDC current consumption | 183mA | 200mA |
| Cable length (unshielded) | 100m |  |
| Input characteristics | Source type, leakage type |  |
| Allowable static current | 1mA |  |
| Insulation test voltage | 500V DC |  |
| Isolation |  |  |
| - Between channel and bus | Yes |  |
| - Between channels | Yes |  |
| Display indication | Green LED display for each channel input |  |
| System power diagnosis and warning | Support |  |
| Operating environment | Operating temperature: -20~60℃, relative humidity: 5%~90% (no condensation) |  |
| Dimensions (length x width x height) | 15×100×80 mm | 30×100×80 mm |

  - Wiring Diagram

    - 4.2.1. SRE1016 Wiring Diagram

PNP wiring

NPN wiring

NPN wiring

PNP wiring

    - 4.2.2. SRE1032 Wiring Diagram

  - Interface Description

    - SRE1016 Indicator Description

| Terminal | Description |
| --- | --- |
| Input1~Input16 | Module input terminal |
| COM1, COM2 | Input public end |

    - SRE1032 Indicator Description

| Terminal | Description |
| --- | --- |
| Input1~Input32 | Module input terminal |
| COM1, COM2 | Input public end |

  - Indicator Description

    - SRE1016 Indicator Description

| Indicator | Description |
| --- | --- |
| PWR (Green) | Module power indicator: On: Module power supply is normal Off: No power supply or abnormal power supply |
| RUN (Green) | Communication indicator: On: Communication is normal Off: Communication is abnormality |
| I1~I16 (Green) | Digital input indicator, the corresponding indicator lights up when the input channel detects a signal. |

    - 4.4.2 SRE1032 Indicator Description

| Indicator | Description |
| --- | --- |
| PWR (Green) | Module power indicator: On: Module power supply is normal Off: Module has no power supply or abnormal power supply |
| RUN (Green) | Communication indicator: On: Communication is normal Off: Communication is abnormal |
| I1~I32 (Green) | Digital input indicator, the corresponding indicator lights up when the input channel detects a signal. |

  - COE General Parameter Description

Module related parameters can be viewed or modified in COE parameters, and parameter set will not be not saved when powered off.

| Parameter | Description |
| --- | --- |
| 2002:01 LocalDI | Parameters are used to set the digital input module and DI delay None: No delay 1.6ms: DI delay is 1.6ms 3.2ms: DI delay is 3.2ms 12.8ms: DI delay is 12.8ms 20ms: DI delay is 20ms 50ms: DI delay is 50ms |
| 2003:01 Fliter time | None: No filtering; 1:1ms； 2:2ms； 3:5ms； 4:10ms； 5:20ms； 6: 50ms. |
| 2004:01 Err 24v_nf | Bit0: 1: Channel 24V power supply is abnormal; 0: Normal. |

- Digital Output Module

  - 16 Point Digital Output Electrical Specifications

SRE2216/SRE2116 digital output module, 16 channel digital output, with module diagnostic function.

| Model | SRE2216 | SRE2116 |
| --- | --- | --- |
| Technical specifications |  |  |
| Type of output | PNP type solid MOSFET | NPN type solid MOSFET |
| Output points | 16 |  |
| Bus 5VDC current consumption | 190mA | 175mA |
| Cable length (unshielded) | 100m |  |
| Output short-circuit protection | Yes, electronic |  |
| Maximum lamp load | 5W |  |
| Output current “1” | 0.5A |  |
| Leakage current | ＜1mA |  |
| Switching frequency |  |  |
| - Resistive load, maximum | 100HZ |  |
| - Inductive load, maximum | 0.5HZ |  |
| - Lamp load, maximum | 10HZ |  |
| - Mechanical load, maximum | --- |  |
| Insulation test voltage | 500V DC |  |
| Isolation |  |  |
| - Between channel and bus | Yes |  |
| - Between channels | Yes |  |
| Display indication | Each channel outputs a green LED display |  |
| System power diagnosis and warning | Support |  |
| Operating environment | Operating temperature: -20~60℃, relative humidity: 5%~90% (no condensation) |  |
| Dimensions (length x width x height ) | 15×100×80（mm） |  |

  - 32 Point Digital Output Electrical Specifications

| Model | SRE2232 | SRE2132 |
| --- | --- | --- |
| Technical specifications |  |  |
| Type of output | PNP type solid MOSFET | NPN type solid MOSFET |
| Output points | 32 |  |
| Bus 5VDC current consumption | 181mA | 175mA |
| Cable length (unshielded) | 100m |  |
| Output short-circuit protection | Yes, electronic |  |
| Maximum lamp load | 5W |  |
| Output current “1” | 0.5A |  |
| Leakage current | ＜1mA |  |
| Switching frequency |  |  |
| - Resistive load, maximum | 100HZ |  |
| - Inductive load, maximum | 0.5HZ |  |
| - Lamp load, maximum | 10HZ |  |
| - Mechanical load, maximum | --- |  |
| Insulation test voltage | 500V DC |  |
| Isolation |  |  |
| - Between channel and bus | Yes |  |
| - Between channels | Yes |  |
| Display indication | Each channel outputs a green LED display |  |
| System power diagnosis and warning | Support |  |
| Operating environment | Operating temperature: -20~60 ℃, relative humidity: 5%~90% (no condensation) |  |
| Dimensions (length x width x height) | 30×80×100（mm） |  |

  - Wiring Diagram

    - 5.3.1. SRE2116 Wiring Diagram

    - 5.3.2. SRE2216 Wiring Diagram

    - 5.3.3. SRE2132 Wiring Diagram

    - 5.3.4. SRE2232 Wiring Diagram

  - Indicator Description

    - SRE2216/SRE2116 Indicator Description

| Indicator | Description |
| --- | --- |
| PWR (Green) | Module power supply indicator: On: The module power supply is normal; Off: The module is powered off; |
| RUN (Green) | Communication indicator: On: Communication is normal Off: Communication is abnormal |
| LED1~LED16 (Green) | Digital output indicator, the corresponding indicator lights up when a signal is detected. |

    - SRE2232/SRE2132 Indicator Description

| Indicator | Description |
| --- | --- |
| PWR (Green) | Module power supply indicator: On: The module power supply is normal; Off: The module is powered off; |
| RUN (Green) | Communication indicator: On: Communication is normal Off: Communication is abnormal |
| LED1~LED32 (Green) | Digital output indicator, the corresponding indicator lights up when a signal is detected. |

  - COE General Parameter Description

| Parameter | Description |
| --- | --- |
| 2001:01 EtherCATBusErrOutoutEN | The parameter is used to set the action of output channel after the module communication is disconnected (this setting will not be saved in case the power is turned off): 0: Maintain the output for 50ms and then clear it; 1: Maintain output; 2: Clear after maintaining the output for 10ms; 3: Clear after maintaining the output for 20ms; 4: Clear after maintaining output for 100ms; 5: Clear after maintaining the output for 500ms; 6: Clear the output immediately; |
| 2004:01 Err 24v_ nf | Bit0: 1: Channel 24V power supply is abnormal; 0: Normal. Bit1: Reserved; Bit2: 1: DO short circuit or overcurrent; 0: Normal. |

- Digital Fast Output Module

SRE5202/SRE5204 digital fast output modules are equipped with DC distributed clock and oversampling functions. The maximum output frequency is 1MHz. They have 2/4-channel outputs respectively, adopt PNP transistors, are rated at 24VDC/0.5A, and also feature a module diagnostic function.

  - Electrical Specifications

| Model |  | SRE5202 |  | SRE5204 |
| --- | --- | --- | --- | --- |
| Technical specifications |  |  |  |  |
| Rated supply voltage |  | 24V DC |  |  |
| Bus 5VDC current consumption |  | 165mA |  | 165mA |
| Load types |  | Resistive Loads, Inductive Loads, Lamp Loads |  |  |
| Oversampling coefficient |  | n = An integer multiple of the cycle time, 1…1000 |  |  |
| Distributed clock |  | <<1μs |  |  |
| Maximum output current |  | 0.5 A per channel (Short-circuit Protection) |  |  |
| Switching time |  | TON:<1μs, TOFF:<1μs |  |  |
| Maximum frequency |  | 1MHz |  |  |
| Current consumption at 24V |  | / |  |  |
| Digital output characteristics |  |  |  |  |
| Number of output points | 2 |  | 4 |  |
| Output type | Transistor PNP Output |  |  |  |
| Isolation |  |  |  |  |
| - Between channels and bus | Yes |  |  |  |
| Display indicators | Green LED display for power supply |  |  |  |
| System power supply diagnosis and warning | Support |  |  |  |
| Operating environment | Operating temperature: - 20~60℃, Relative humidity: 5%~90% (no condensation) |  |  |  |
| Dimensions (length x width x height) | 15×100×80（mm） |  |  |  |

  - Wiring Diagram

    - SRE5202 Wiring Diagram

    - SRE5204 Wiring Diagram

  - 6.3. Terminal Description

    - 6.3.1. SRE5202 Terminal Description

| Wiring terminal | Description |
| --- | --- |
| Output1 | Digital output channel 1 |
| Output2 | Digital output channel 2 |
| 24V | Sensor power supply positive pole |
| 0V | Sensor power supply negative pole |
| PE | Shielded wire |

    - 6.3.2. SRE5204 Terminal Description

| Wiring terminal | Description |
| --- | --- |
| Output1 | Digital output channel 1 |
| Output2 | Digital output channel 2 |
| Output3 | Digital output channel 3 |
| Output4 | Digital output channel 4 |
| 24V | Sensor power supply positive pole |
| 0V | Sensor power supply negative pole |
| PE | Shielded wire |

  - 6.4. Indicator Description

    - 6.4.1. SRE5202 Indicator Description

| Indicator | (Description) |
| --- | --- |
| PWR (Green) | Module power indicator: On: Normal power supply Off: Abnormal power supply |
| RUN (Green) | Communication indicator: On: Normal communication Off: Abnormal communication |
| LED1 | Output1 output indicator On: Output1 is outputting Off: Output1 is not outputting |
| LED2 | Output2 output indicator On: Output2 is outputting Off: Output2 is not outputting |

    - 6.4.2. SRE5204 Indicator Description

| Indicator | Description |
| --- | --- |
| PWR (Green) | Module power indicator: On: The power supply is normal. Off: The power supply is abnormal. |
| RUN (Green) | Communication indicator: On: The communication is normal. Off: The communication is abnormal. |
| LED1 | Output1 output indicator On: Output1 is outputting. Off: Output1 is not outputting. |
| LED2 | Output2 output indicator On: Output2 is outputting. Off: Output2 is not outputting. |
| LED3 | Output3 output indicator On: Output3 is outputting. Off: Output3 is not outputting. |
| LED4 | Output4 output indicator On: Output4 is outputting. Off: Output4 is not outputting. |

  - 6.5. Parameter Description

    - 6.5.1. COE Parameter Description

| Parameter | Description |
| --- | --- |
| 2001:01 EtherCATBusErrOutoutEN | Parameters are used to set the action of the output channel after the module communication is disconnected (not saved after power outrage): 0: Maintain the output for 50ms and then clear it; 1: Maintain output; 2: Clear after maintaining the output for 10ms; 3: Clear after maintaining the output for 20ms; 4: Clear after maintaining the output for 100ms; 5: Clear after maintaining the output for 500ms; 6: Clear the output immediately; |

    - 6.5.2. DC/Oversampling Parameter Description

After the parameters are set, refresh to take effect.

| Parameter | Description |  |
| --- | --- | --- |
| Operation Mode: | Channel usage selection: 2 Channels (Byte): Select to use two channels, Byte type. 2 Channels (Bit): Select to use two channels, Bit type. 1 Channels (Byte): Select to use one channel, Byte type (first channel). 1 Channels (Bit): Select to use one channel, Bit type (first channel). Note: When using SRE5204 module, if 1 Channels is selected, the first two channels will be used; if 2 Channels are selected, all channels will be used. |  |
| Sync Unit Cycle Time (us): | Cycle time, which is determined by the cycle time set by EtherCAT. |  |
| Oversampling Factor: | 1, 2, 4, 5, 8, 10, 16, 20, 25, 32, 40, 50, 64, 80, 100, 125, 128; | Sampling data of (Bit type) |
|  | 8(1*8), 16(2*8), 32(4*8), 40(5*8), 64(8*8), 80(10*8), 128(16*8), 160(20*8), 200(25*8) | Sampling data of (Bit type) |
| Sample Cycle Time (us): | Sampling cycle, which is determined by the relationship between the cycle time set by EtherCAT and the number of samples. |  |

    - 6.5.3. Codesys/Distributed Clocks

(When using SRE5204 module, if 1 Channels is selected, the first two channels will be used; if 2 Channels are selected, all channels will be used.)

| Operation Mode |  | Remark |
| --- | --- | --- |
| 1 Ch. - X times oversampling | X:2, 3, 4, 5, 8, 10, 16, 20, 40, 50, 100, 200, 400, 1000 | Sampled data for channel 1 (bit type). |
| 2 Ch. - X times oversampling | X:2, 3, 4, 5, 8, 10, 16, 20, 40, 50, 100, 200, 400, 1000 | Sampled data for channel 1and 2 (bit type). |

- Digital Input/Output Module

  - Electrical Specifications

SRE digital input/output module, 16 digital inputs, 16 digital outputs, NPN/PNP type, module with diagnostic function.

| Model |  | SRE1332 |  |  | SRE1432 |
| --- | --- | --- | --- | --- | --- |
| Technical specifications |  |  |  |  |  |
| Bus 5VDC current consumption | 205mA |  |  | 200mA |  |
| Input characteristics |  |  |  |  |  |
| Input points | 16 |  |  |  |  |
| - Limit value | 24V DC |  |  |  |  |
| - Signal “0” | Maximum 5V DC, 1mA |  |  |  |  |
| - Signal “1” | Minimum 15V DC, 2.5mA |  |  |  |  |
| Input characteristics | Leakage type |  |  | Source type |  |
| Allowable static current | 1mA |  |  |  |  |
| Insulation test voltage | 500V DC |  |  |  |  |
| Cable length (unshielded) | Maximum length 300m |  |  |  |  |
| Cable length (shielding) | Maximum length 500m |  |  |  |  |
| Output |  |  |  |  |  |
| Type of output |  | NPN type solid MOSFET | PNP type solid MOSFET |  |  |
| Output points |  | 16 |  |  |  |
| Cable length (unshielded) |  | Maximum length 300m |  |  |  |
| Cable length (shielding) |  | Maximum length 500m |  |  |  |
| Output short-circuit protection |  | Yes, electronic |  |  |  |
| Maximum lamp load |  | 5W |  |  |  |
| Output current “1” |  | 0.5A |  |  |  |
| Leakage current |  | ＜1mA |  |  |  |
| Contact mechanical lifespan |  | -- |  |  |  |
| Contact electrical life (rated load) |  | -- |  |  |  |
| Switching frequency |  |  |  |  |  |
| - Resistive load, maximum | 100HZ |  |  |  |  |
| - Inductive load, maximum | 0.5HZ |  |  |  |  |
| - Lamp load, maximum | 10HZ |  |  |  |  |
| - Mechanical load, maximum | -- |  |  |  |  |
| Insulation test voltage | 500V DC |  |  |  |  |
| Isolation |  |  |  |  |  |
| - Between channel and bus |  | Yes |  |  |  |
| - Between channels |  | Yes |  |  |  |
| Display indication |  | Each channel output green LED display |  |  |  |
| System power diagnosis and warning |  | Support |  |  |  |
| Operating environment |  | Operating temperature: -20~60℃, relative humidity: 5%~90% (no condensation) |  |  |  |
| Dimensions (length x width x height) |  | 30×100×80（mm） |  |  |  |

  - Wiring Diagram

    - SRE1332 Wiring Diagram

NPN wiring

NPN wiring

    - SRE1432 Wiring Diagram

PNP wiring

PNP wiring

  - Indicator Description

| Indicator | Description |
| --- | --- |
| PWR (Green) | Module Power Indicator: On: The module power supply is normal; Off: The module is powered off; |
| RUN (Green) | Communication indicator: On: Communication is normal Off: Communication is abnormal |
| I1~I16 (Green) | The digital input indicator will turn on when a signal is detected. |
| Q1~Q16 (Green) | Digital output indicator, the corresponding indicator lights up when a signal is detected. |

  - COE General Parameter Description

| Parameter | Description |
| --- | --- |
| 2001:01 EtherCATBusErrOutoutEN | Parameters are used to set the action of the output channel after the module communication is disconnected: 0: Maintain the output for 50ms and then clear it; 1: Maintain output; 2: Clear after maintaining the output for 10ms; 3: Clear after maintaining the output for 20ms; 4: Clear after maintaining the output for 100ms; 5: Clear after maintaining the output for 500ms; 6: Clear the output immediately; |
| 2002:01 LocalDI | Parameters are used to set the digital input module and DI delay None: No delay 1.6ms: DI delay is 1.6ms 3.2ms: DI delay is 3.2ms 12.8ms: DI delay is 12.8ms 20ms: DI delay is 20ms 50ms: DI delay is 50ms |
| 2003:01 Fliter time | None: No filtering; 1:1ms； 2:2ms； 3:5ms； 4:10ms； 5:20ms； 6:50ms. |
| 2004:01 Err 24v_nf | Bit0: 1: Channel 24V power supply is abnormal; 0: Normal. Bit1: Reserved; Bit2: 1: DO short circuit or overcurrent; 0: Normal. |

- Analog Rapid Acquisition Input Module

SRE3522 two-way analog fast acquisition module, does not support Omron platform.

  - Electrical Specifications

| Model | SRE3522 |
| --- | --- |
| Technical specifications |  |
| Supply voltage | 18~28V DC |
| Bus 5VDC current consumption | 187mA |
| Number of input channels | 2 |
| Collection type | Voltage |
| Range |  |
| Voltage | -10V-10V |
| Data word |  |
| Bipolar | -32000~32000 |
| Resolution | 16 bits |
| Input type | Differential input |
| Sampling type | Simultaneously |
| Oversampling coefficient | N=1... 100 optional (up to 100 ksamples/s) |
| Maximum sampling rate | Maximum 10 µ s/100 ksps (per channel, synchronous) |
| Isolation |  |
| - Between channel and bus | Yes |
| Display indication | Power supply green LED display |
| Distributed clock | Support |
| System power diagnosis and warning | Support |
| Operating environment | Operating temperature: -20~60℃, relative humidity: 5%~90% (no condensation) |
| Anti-vibration/anti-impact performance | Comply with EN 60068-2-6/EN 60068-2-27 standards |
| Anti-electromagnetic interference/anti-electromagnetic radiation performance | Comply with EN 61000-6-2/EN 61000-6-4 standards |
| Sampling type | Simultaneously |
| Dimensions (length x width x height) | 15×100×80 mm |

  - SRE3522 Module Wiring Diagram

  - Indicator Description

| Indicator | Description |
| --- | --- |
| PWR (Green) | Module power indicator: On: Power supply is normal Off: Abnormal power supply or module not powered |
| NET (Green) | Communication indicator: On: Communication is normal Off: Communication is abnormal |

  - Terminal Description

| Terminal | Description |
| --- | --- |
| A+, A- | CH0 voltage acquisition input terminal |
| B+, B- | CH1 voltage acquisition input terminal |

  - Parameter Description

The signal oversampling period is: Sample Cycle Time=Sync Unit Cycle Time/Oversampling Factor, with a minimum sampling period of 10us for sampling. For example, if the bus cycle time is 1000us and the sampling frequency is 100 times, the sampling period is 10us. A value is sampled per 10 us and execute 100 times, and this data is accumulated and transmitted in the next bus cycle.

| Parameter | Description |
| --- | --- |
| Operation Mode: | Select the number of channels used: 2 Channels: Select two channels 1 Channel: Select one channel (first channel) |
| Sync Unit Cycle Time (us): | Cycle time, determined by EtherCAT's set cycle time |
| Oversampling Factor: | Sampling frequency per cycle: up to 100 times can be collected 1:1 2:2 3:4 4:5 5:8 6:10 7:16 8:20 9:25 10:32 11:40 12:50 13:64 14:80 15:100 |
| Sample Cycle Time (us): | The sampling cycle is determined by the relationship between the EtherCAT set cycle and the quantity of samples |

- Analog Input Module

  - Electrical Specifications

High performance analog input module, 16 bit accuracy, 4/8 channel voltage/current input, with module diagnostic function.

| Model | SRE3204 | SRE3208 |
| --- | --- | --- |
| Technical specifications |  |  |
| Supply voltage | 18~28V DC |  |
| Bus 5VDC current consumption | 160mA | 165mA |
| Number of input channels | 4 | 8 |
| Input type | Voltage/Current |  |
| Range |  |  |
| Voltage (unipolar) | 0-10V |  |
| Voltage (Bipolar) | -10V-10V |  |
| Current | 0~20mA |  |
| Data word |  |  |
| Unipolar | 0~32000 |  |
| Bipolar | -32000~32000 |  |
| Isolation |  |  |
| - Between channel and bus | Yes |  |
| Display indication | Power supply green LED display |  |
| System power diagnosis and warning | Support |  |
| Operating environment | Operating temperature: -20~60℃, relative humidity: 5%~90% (no condensation) |  |
| Dimensions (length x width x height) | 15×100×80 mm | 30×100×80 mm |

  - Module Wiring Diagram

    - SRE3204 Wiring Diagram

Note: A+ and A - are voltage signal input channels, and AI+ and AI- current signal input channels. If CH0 needs to be connected to voltage signal, it shall be connected with A+ and A - terminals; If CH0 needs to be connected to current signal, it shall be connected with AI+ and AI - terminals; These two channels are both CH0 and occupy the same data address, so only one can be used and cannot be connected simultaneously. The other input channels follow this rule. The wiring in the diagram is only an example, and the specific usage can be connected according to one’s own needs.

    - SRE3208 Wiring Diagram

Note: A+ and A - are voltage signal input channels, and AI+ and AI- current signal input channels. If CH0 needs to be connected to voltage signal, it shall be connected with A+ and A - terminals; If CH0 needs to be connected to current signal, it shall be connected with the AI+and AI - terminals; These two channels are both CH0 and occupy the same data address, so only one can be used and cannot be connected simultaneously. The other input channels follow this rule. The wiring on the diagram is only an example, and the specific usage can be connected according to one’s own needs.

  - Terminal Description

    - SRE3204 Terminal Description

| Terminal | Description |
| --- | --- |
| A+, A- | CH0 voltage input terminal |
| AI+, AI- | CH0 current input terminal |
| B+, B- | CH1 voltage input terminal |
| BI+, BI- | CH1 current input terminal |
| C+, C- | CH2 voltage input terminal |
| CI+, CI- | CH2 current input terminal |
| D+, D- | CH3 voltage input terminal |
| DI+, DI- | CH3 current input terminal |

    - SRE3208 Terminal Description

| Terminal | Description |
| --- | --- |
| A+, A- | CH0 voltage input terminal |
| AI+, AI- | CH0 current input terminal |
| B+, B- | CH1 voltage input terminal |
| BI+, BI- | CH1 current input terminal |
| C+, C- | CH2 voltage input terminal |
| CI+, CI- | CH2 current input terminal |
| …… | ……… |
| ……… | ……… |
| H+, H- | CH7 voltage input terminal |
| HI+, HI- | CH7 current input terminal |

  - Indicator Description

| Indicator | Description |
| --- | --- |
| PWR (Green) | Module power indicator: On: The module power supply is normal; Off: The module is powered off; |
| RUN (Green) | Communication indicator: On: Communication is normal Off: Communication is abnormal |

  - COE General Parameter Description

The configuration parameters will not be synchronized to Startup, and they will not be saved after power failure or hot plugging.

| Parameter | Data type | Description |
| --- | --- | --- |
| 2004:01 | Err 24v_nf | Bit0: 1: Channel 24V power supply is abnormal; 0: Normal. |
| 2005:01 | Channel Num | 0: Enable 4 channels; 1: Enable the first channel; 2: Enable the first two channels; |
| 2005:02 | Channel Time | Channel update time: 0:400us； 1:lms； 2:2ms； 3:5ms； 4:10ms； 5:20ms； |
| 2005:03 | Channel Type | Each BIT corresponds to a channel: for example, Bit0: corresponds to CH0; Bit1: corresponds to CH1; ........ Set detection value: 0: Voltage ± 10V; 1: Current 0-20mA; |

- Analog Output Module

  - Electrical Specifications

SRE4204 analog output module, 4-channel voltage/ current, ± 10V or 0-20mA, module diagnostic function, 16 bit accuracy, 35mm rail installation.

| Model | SRE4204 | SRE4208 |
| --- | --- | --- |
| Supply voltage | 18~28V DC |  |
| Bus 5VDC current consumption | 170mA | 170mA |
| Number of output channels | 4 | 8 |
| Range |  |  |
| Voltage (Unipolar) | 0~10V |  |
| Voltage (Bipolar) | -10~10V |  |
| Current | 0~20mA |  |
| Voltage | -32000~32000, full range |  |
| Current | 0~32000, full range |  |
| Isolation |  |  |
| - Between channel and bus | Yes |  |
| Display indication | Power supply green LED display |  |
| System power diagnosis and warning | Support |  |
| Operating environment | Operating temperature: -20~60℃, relative humidity: 5%~90% (no condensation) |  |
| Dimensions (length x width x height) | 15×100×80 mm | 30×100×80 mm |

  - Module Wiring Diagram

    - SRE4204 Wiring Diagram

    - SRE4208 Wiring Diagram

  - Indicator Description

| Indicator | Description |
| --- | --- |
| PWR (Green) | Module power indicator: On: The module power supply is normal; Off: The module is powered off; |
| RUN (Green) | Communication indicator: On: Communication is normal Off: Communication is abnormal |

  - Terminal Description

    - SRE4204 Terminal Description

| Terminal | Description |
| --- | --- |
| V0, M0 | CH0 voltage output terminal |
| I0, M0 | CH0 current output terminal |
| V1, M1 | CH1 voltage output terminal |
| I1, M1 | CH1 current output terminal |
| V2, M2 | CH2 voltage output terminal |
| I2, M2 | CH2 current output terminal |
| V3, M3 | CH3 voltage output terminal |
| I3, M3 | CH3 current output terminal |

    - SRE4208 Terminal Description

| Terminal | Description |
| --- | --- |
| V0, M0 | CH0 voltage output terminal |
| I0, M0 | CH0 current output terminal |
| V1, M1 | CH1 voltage output terminal |
| I1, M1 | CH1 current output terminal |
| V2, M2 | CH2 voltage output terminal |
| I2, M2 | CH2 current output terminal |
| V3, M3 | CH3 voltage output terminal |
| I3, M3 | CH3 current output terminal |
| V4, M4 | CH4 voltage output terminal |
| I4, M4 | CH4 current output terminal |
| V5, M5 | CH5 voltage output terminal |
| I5, M5 | CH5 current output terminal |
| V6, M6 | CH6 voltage output terminal |
| I6, M6 | CH6 current output terminal |
| V7, M7 | CH7 voltage output terminal |
| I7, M7 | CH7 current output terminal |

  - COE General Parameter Description

| Parameter | Data type | Description |
| --- | --- | --- |
| 2001:01 | EtherCATBusErrOutputEN | Parameters are used to set the action of the output channel after the module communication is disconnected: 0: Maintain the output for 50ms and then clear it; 1: Maintain output; 2: Clear after maintaining the output for 10ms; 3: Clear after maintaining the output for 20ms; 4: Clear after maintaining output for 100ms; 5: Clear after maintaining the output for 500ms; 6: Clear the output immediately; |
| 2004:01 | Err 24v_nf | Bit0: 1: Channel 24V power supply is abnormal; 0: Normal. |
| 2005:01 | Channel Type | Each BIT corresponds to a channel: for example, Bit0: corresponds to CH0; Bit1: corresponds to CH1; ........ Set channel range configuration: 0: ±10V 1:0-20mA/0-10V |

- Temperature Measurement Module

  - Thermocouple Measurement Module SRE3284

    - Electrical Specifications

| Model | SRE3284 |
| --- | --- |
| Technical specifications |  |
| Number of input points | 4 |
| Input type | Thermocouple |
| Power supply polarity protection | Support |
| Operating voltage | 24VDC (Allowable voltage range: 18VDC~28VDC) |
| Bus 5VDC current consumption | 165mA |
| Input range | Thermocouple types (select one): S/T/R/E/N/K/J; Voltage range: ±80mV |
| Measurement principle | Sigma - Delta |
| Resolution |  |
| Temperature | 0.1℃/0.1℉ |
| Voltage | 15 bits + sign bit |
| Common mode rejection | 85dB, DC-50HZ/60HZ/400HZ |
| Wire length | The longest compensation wire is 30m |
| Wire loop resistance | Maximum 20Ω |
| Input impedance | ≥10MΩ |
| Basic error | ≤0.1%FS |
| Conformance | 0.05%FS |
| Cold junction error | ±1.5℃ |
| Isolation |  |
| - Between channel and bus | Yes |
| - Between power supply and bus | Yes |
| - Between channel and power supply | Yes |
| Display indication | Power and RUN green indicator lights |
| Operating environment |  |
| Operating temperature | Operating temperature: -20~60℃, Relative humidity:5%~90% (no condensation) |
| Dimensions (length × width × height) | 15×100×80（mm） |

    - Module Wiring Diagram

External NC compensation

    - Terminal Description

| Terminal | Description |
| --- | --- |
| A+ A- | CH0 thermocouple input terminal |
| B+ B- | CH1 thermocouple input terminal |
| C+ C- | CH2 thermocouple input terminal |
| D+ D- | CH3 thermocouple input terminal |
| NTC+ NTC- | External NTC compensation |

    - Indicator Description

| Indicator | Description |
| --- | --- |
| PWR (Green) | Module power indicator: On: The module power supply is normal; Off: The module is powered off; |
| RUN (Green) | Communication indicator: On: Communication is normal Off: Communication is abnormal |
| S1 (Red) | Channel disconnection detection light: Flashing: CH0 sampling value is out of range or disconnected. Off: CH0 sampling value detection value is within the normal range. |
| … | … |
| S4 (Red) | Channel disconnection detection light: Flashing: CH3 sampling value is out of range or disconnected. Off: CH3 sampling value is within the normal range. |

    - COE Parameter Description

| Parameter | Data type | Description |
| --- | --- | --- |
| 2004:01 | Err 24v_nf | Bit0: 1: Channel 24V power supply is abnormal; 0: Normal. |
| 2005:01 | Channel_Type | Configure the channel thermocouple type, divided into 8 types: 0:J； 1:K； 2:T； 3:E； 4:R； 5:S； 6:N； 7:+/-80MV； |
| 2005:02 | cali_depth | Filter level: 0: Hight: strong filtering; 1: Normal: normal filtering; 2: None: no filtering; |
| 2005:03 | TC_no_compensate | Whether to perform cold junction compensation: 0: Yes; 1: No; |
| 2005:04 | Meth_compensate | Temperature compensation mode: 0: none: internal compensation; 1: outside as NTC: external NTC compensation; |

  - Thermal Resistance Measurement Module SRE3274

    - Electrical Specifications

| Model | SRE3274 |
| --- | --- |
| Technical specifications |  |
| Number of input points | 4 |
| Input type | Thermal resistors |
| Power supply linear protection | Support |
| Maximum sustainable voltage | 30V DC |
| Bus 5VDC current consumption | 165mA |
| Input range | RTD Type (choose one): Pt-100Ω,1000Ω (α=3850PPM,3920PPM, 3850.55PPM,3916PPM,3902PM); Ni-100Ω,1000Ω(α=6720PPM,6178PPM); |
| Measurement principle | Sigma-Delta |
| Data word | -32768~+32767 |
| Resolution |  |
| Temperature | 0.1℃/0.1℉ |
| Voltage |  |
| Resistance | 15 bits + sign bit |
| Measurement conversion time | < 400ms |
| Common mode rejection | > 125dB, AC120V |
| Cable length (compensation lead) | Up to 30m |
| Wire loop resistance | Maximum 100Ω |
| Input impedance | ≥1MΩ |
| Basic error | ≤0.1%FS |
| Conformance | 0.05%FS |
| Cold junction error | --- |
| Isolation |  |
| - Between channel and bus | Yes |
| - Between power supply and bus | Yes |
| - Between channel and power supply | Yes |
| Display indication | Power supply green LED display |
| System power diagnostics and warnings | Support |
| Operating environment | Operating temperature: - 20~60℃, Relative humidity: 5%~90% (no condensation |
| Dimensions (length x width x height) | 15×100×80 mm |

    - Module Wiring Diagram

    - 11.2.3. Terminal Description

| Terminal | Description |
| --- | --- |
| A+, A-, a- | CH0 Thermal resistor input terminal |
| B+, B-, b- | CH1 Thermal resistor input terminal |
| C+, C-, c- | CH2 Thermal resistor input terminal |
| D+, D-, d- | CH3 Thermal resistor input terminal |

    - 11.2.4. Indicator Description

| Indicator | Description |
| --- | --- |
| PWR (Green) | Module power indicator: On: The module power supply is normal; Off: The module is powered off; |
| RUN (Green) | Communication indicator: On: Communication is normal Off: Communication is abnormal |
| S1 (Red) | Channel disconnection detection light: Flashing: CH0 sampling value is out of range or disconnected. Off: CH0 sampling value detection value is within the normal range. |
| …… | …… |
| S4 (Red) | Channel disconnection detection light: Flashing: CH3 sampling value is out of range or disconnected. Off: CH3 sampling value is within the normal range. |

    - 11.2.5. COE Parameter Description

| Parameter | Data type | Description |
| --- | --- | --- |
| 2004:01 | Err 24v_nf | Bit0: 1: Channel 24V power supply is abnormal; 0: Normal. |
| 2005:01 | RTD_Ttype | Thermal resistor type: 0:100Ω Pt 0.003850(Default) 1:1000Ω Pt 0.003850 2:100Ω Pt 0.003920 3:1000Ω Pt 0.003920 4:100Ω Pt 0.00385055 5:1000Ω Pt 0.00385055 6:100Ω Pt 0.003916 7:1000Ω Pt 0.003916 8:100Ω Pt 0.003902 9:1000Ω Pt 0.003902 11:100Ω Ni 0.006720 12:1000Ω Ni 0.006720 13:100Ω Ni 0.006178 14:1000Ω Ni 0.006178 |
| 2005:01 | Red_led_en | Disconnection detection alarm: Bit0: LED indicate Ch1: Bit1: LED indicate Ch2: Bit2: LED indicate Ch3: Bit3: LED indicate Ch4: Definition: 0: Enable disconnection detection alarm 1: Disable disconnection detection alarm |

- Power Relay Module SRE9001

The SRE power relay module serves as a 24VDC power relay and also as a 5VDC isolated bus power relay. It has no system diagnosis or alarm functions and does not occupy a slot number.

  - Electrical Specifications

| Model | SRE9001 |
| --- | --- |
| Power specifications |  |
| Input supply voltage | 24VDC (±20%) |
| Output system voltage | 5VDC ± 3% (Extension module power supply) |
| Output system current | 10A |
| authentication | CE |
| Physical properties |  |
| Operating temperature | Operating temperature: - 20~60℃, relative humidity: 5%~90% (no condensation) |
| Storage temperature | -25~+85℃ |
| Relative humidity | 95%, no condensation |
| Protection level | IP20 |
| Occupied slots | Not occupied |
| System diagnostics and alarms | Not support |
| Dimensions (length x width x height) | 15×100×80（mm） |

  - Module Wiring Diagram

  - Indicator Description

| Indicator | Description |
| --- | --- |
| 24V (Green) | Module power indicator: On: The module power supply is normal; Off: The module is powered off; |
| 5V (Green) | Bus source indicator: On: Communication is normal Off: Communication is abnormal |

  - Terminal Description

| Terminal | Description |
| --- | --- |
| Us 24V | System power positive pole |
| Us 0V | System power negative pole |
| Up 24V | IO channel power positive pole |
| Up 0V | IO channel power negative pole |
| PE | Ground |

- Serial Port Module

SRE6002/SRE6004 serial communication modules support high-speed buses. SRE6002 module comes with 2 serial ports, while SRE6004 module is equipped with 4 serial ports. The serial ports support full-duplex (RS422/RS232) and half-duplex (RS485) modes. Each serial port can independently support the Modbus-RTU master-slave station and free port protocol.

  - Electrical Specifications

| Model | SRE6002 | SRE6004 |
| --- | --- | --- |
| Technical specifications |  |  |
| Bus 5VDC current consumption | 170mA | 170mA |
| Interface | 2 RS422 /RS232 /RS485 interfaces | 4 RS422/RS232/RS485 interfaces |
| Serial port support protocol | Modbus-RTU master, slave, free port protocol |  |
| Data transmission rate | 1200bps, 2400bps, 4800bps, 9.6Kbps, 19.2Kbps, 38.4Kbps, 57.6Kbps, 115.2Kbps |  |
| Parity bit | No parity, odd parity, even parity |  |
| Stop bit | 1, 2 |  |
| Data bit | 7, 8 |  |
| Bus 5V DC current consumption | <70mA |  |
| Distributed clock | Not support |  |
| Isolation |  |  |
| Between channels and buses | Yes |  |
| Display indication | Power supply green LED display |  |
| Operating environment | Operating temperature: -20~55℃, relative humidity: 5%~90% (no condensation) |  |
| Dimensions (length× width × height) | 15×100×80（mm） | 30×100×80（mm） |

  - Module Wiring Diagram

    - SRE6002 Wiring Diagram

Note: One channel only supports the connection of one type of serial port at the same time. The wiring shown in the diagram is for illustrative purposes only. The specific wiring method should be carried out according to the actual usage.

    - SRE6004 Wiring Diagram

Note: One channel only supports the connection of one type of serial port at the same time. The wiring shown in the diagram is for illustrative purposes only. The specific wiring method should be carried out according to the actual usage.

  - Indicator Description

    - SRE6002 Indicator Description

| Indicator | Description |
| --- | --- |
| PWR (Green) | Module power indicator: On: The module power supply is normal; Off: The module is powered off; |
| RUN (Green) | Communication indicator: On: Communication is normal Off: Communication is abnormal |
| RX1/TX1 | COM1 serial port receiving and sending indicator light, the indicator light flashes when data is being sent or received; |
| RX2/TX2 | COM2 serial port receiving and sending indicator light, the indicator light flashes when data is being sent or received; |

    - SRE6004 Indicator Description

| Indicator | Description |
| --- | --- |
| PWR (Green) | Module power indicator: On: The module power supply is normal; Off: The module is powered off; |
| RUN (Green) | Communication indicator: On: Communication is normal Off: Communication is abnormal |
| RX1/TX1 | COM1 serial port transceiver indicator, the indicator flashes when data is being sent or received; |
| RX2/TX2 | COM2 serial port transceiver indicator, the indicator flashes when data is being sent or received; |
| RX3/TX3 | COM3 serial port transceiver indicator, the indicator flashes when data is being sent or received; |
| RX4/TX4 | COM4 serial port transceiver indicator, the indicator flashes when data is being sent or received; |

  - Module Terminal Description

    - SRE6002 Terminal Description

| Terminal | Terminal description |  |
| --- | --- | --- |
| R1+/A1 | COM1 serial port RS422 signal receiving + | COM1serial port RS485 signal receiving A+ |
| T1+ | COM1 serial port RS422 signal sending + |  |
| R1-/B1 | COM1 serial port RS422 signal receiving - | COM1serial port RS485 signal receiving B- |
| T1- | COM1 serial port RS422 signal sending - |  |
| R1 | COM1 serial port RS232 signal receiving |  |
| T1 | COM1 serial port RS232 signal sending |  |
| GND | COM1 serial port RS232 signal GND |  |
| PE | Ground |  |
| R2+/A2 | COM2 serial port RS422 signal receiving + | COM2 serial port RS485 signal receiving A+ |
| T1+ | COM2 serial port RS422 signal sending + |  |
| R2-/B2 | COM2 serial port RS422 signal receiving - | COM2 serial port RS485 signal receiving B- |
| T2- | COM2 serial port RS422 signal sending - |  |
| R2 | COM2 serial port RS232 signal receiving |  |
| T2 | COM2 serial port RS232 signal sending |  |
| GND | COM2 serial port RS232 signal GND |  |
| PE | Ground |  |

    - SRE6004 Terminal Description

| Terminal | Terminal Description |  |
| --- | --- | --- |
| R1+/A1 | COM1 serial port RS422 signal receiving + | COM1serial port RS485 signal receiving A+ |
| T1+ | COM1 serial port RS422 signal sending + |  |
| R1-/B1 | COM1 serial port RS422 signal receiving - | COM1serial port RS485 signal receiving B- |
| T1- | COM1 serial port RS422 signal sending - |  |
| R1 | COM1 serial port RS232 signal receiving |  |
| T1 | COM1 serial port RS232 signal sending |  |
| GND | COM1 serial port RS232 signal GND |  |
| PE | Ground |  |
| R2+/A2 | COM2 serial port RS422 signal receiving + | COM2serial port RS485 signal receiving A+ |
| T1+ | COM2 serial port RS422 signal sending + |  |
| R2-/B2 | COM2 serial port RS422 signal receiving - | COM2serial port RS485 signal receiving B- |
| T2- | COM2 serial port RS422 signal sending - |  |
| R2 | COM2 serial port RS232 signal receiving |  |
| T2 | COM2 serial port RS232 signal sending |  |
| GND | COM2 serial port RS232 signal GND |  |
| PE | Ground |  |
| R3+/A3 | COM3 serial port RS422 signal receiving + | COM3serial port RS485 signal receiving A+ |
| T3+ | COM3 serial port RS422 signal sending + |  |
| R3-/B3 | COM3 serial port RS422 signal receiving - | COM3serial port RS485 signal receiving B- |
| T3- | COM3 serial port RS422 signal sending - |  |
| R3 | COM3 serial port RS232 signal receiving |  |
| T3 | COM3 serial port RS232 signal sending |  |
| GND | COM3 serial port RS232 signal GND |  |
| PE | Ground |  |
| R4+/A4 | COM4 serial port RS422 signal receiving + | COM4serial port RS485 signal receiving A+ |
| T4+ | COM4 serial port RS422 signal sending + |  |
| R4-/B4 | COM4 serial port RS422 signal receiving - | COM4serial port RS485 signal receiving B- |
| T4- | COM4 serial port RS422 signal sending - |  |
| R4 | COM4 serial port RS232 signal receiving |  |
| T4 | COM4 serial port RS232 signal sending |  |
| GND | COM4 serial port RS232 signal GND |  |
| PE | Ground |  |

  - Parameter Description

    - COE General Parameter Description

| Parameter | Description |
| --- | --- |
| 2001:01 EtherCATBusErrCOMEN | The parameter is used to set whether COM can send and receive data normally after the module communication is disconnected: 0: COM cannot send and receive data normally after ECT is disconnected; 1: COM can send and receive data normally after ECT is disconnected; |

    - Parameter Description

SRE6002 and SRE6004 are serial port modules with 2 and 4 serial ports respectively. Their parameter descriptions are the same. Illustrated by SRE6004, SRE6002 can be configured and used by referring to this. All parameter changes will take effect immediately, and there is no need to power off and restart, as shown in the following figure:

| Parameter | Description |
| --- | --- |
| Duplex Mode | 0: Full duplex (RS232 &== & RS422) 1: Half duplex (RS485) |
| Baudrate | Baud Rate: 0:1200 1:2400 2:4800 3:9600 4:19200 5:38400 6:57600 7:115200 |
| Data Bit | Data bits: 0:8 bits 1:7 bits |
| Stop Bit | Stop bits: 0:1 bits 1:2 bits |
| Parity Bit | Parity bit: 0: No parity 1: Odd parity 2: Even parity |
| ReceiveTimeout | Serial port receive timeout: 5-200 (unit: ms) If the range is exceeded, it will be calculated according to the range. For example, if it exceeds 200, it will be calculated as 200. |
| Modbus Master ResponseTimeout | Modbus RTU master mode response timeout If the slave does not respond within the set time, the communication is considered to have timed out; 5-5000 (unit: ms) If the range is exceeded, it will be calculated according to the range. For example, if it exceeds 5000, it will be calculated as 5000. |
| Modbus Master Scan Time | Modbus RTU Master Mode Polling Time In MBS Master Mode, the interval between a completed instruction and the next instruction; unit: ms. |

  - Configuration Module Description

Each serial port can be independently configured as Modbus master station, Modbus slave station, or free port. The maximum number of modules that can be configured for the Modbus master station is 32. The maximum number of modules that can be configured for the Modbus slave station is 1. And the maximum number of modules that can be configured for the free port is 1.

    - Modbus Master Configuration

In the Slot, select the module corresponding to the serial port and add the module you want to configure. For example, add "Read 32 Words 4xxxx" to Serial Port 1. Each serial port can configure up to 32 modules when the allocation is reasonable, as shown in the following figure:

After the configuration is completed, add the refresh IO, and then it can be operated (OP). The illustration is as follows:

| State | Module status: 1: Communication is normal 2: Communication timeout 3: CRC error 4: Function code or address error |
| --- | --- |
| Output Data | Output address: Output Data 1~ Output Data x |
| Slave ID | The ID of the slave to be accessed |
| Addr | The Modbus address to be accessed |

| Input Data | Input address: Input Data 1~ Input Data x |
| --- | --- |
| State | Module status: 1: Communication is normal 2: Communication timeout 3: CRC error 4: Function code or address error |
| Slave ID | The ID of the slave to be accessed |
| Addr | The address of the Modbus to be accessed |

    - Modbus Slave Configuration

In the Slot, select the module corresponding to the relevant serial port and add the slave station module that you want to configure. Each serial port can configure at most 1 module. If the number of configured modules is greater than 1, OP cannot be carried out, as shown in the following figure:

After the configuration is completed, add the refresh IO, and then OP can be carried out, as shown in the following figure:

| Parameter | Description |
| --- | --- |
| Input Datas: | Input Data 1~ Input Data x The data area written by Modbus RTU master station is allowed and the starting address is 40256. |
| Output Datas: | Output Data 1~ Output Data x The data area read by Modbus RTU master station is allowed and the starting address is 40001. |
| Slave ID: | ID of the local slave station |

    - Free Port Configuration

In the Slot, select the module corresponding to the relevant serial port and add it. Each serial port can be configured with a maximum of 1 module. If the number of configured modules is greater than 1, OP cannot be carried out, as shown in the following figure:

Input parameter description:

| Meaning of status words | Transmit Done: The current frame data has been sent; |
| --- | --- |
|  | Receive request: There is new data to receive; |
|  | Init accepted: The serial port has been reinitialized; |
|  | SndBuffer full: The length of the sent frame exceeds 1024; |
|  | PutData Done: Writing the sent data to the send buffer is completed; |
|  | Input length: The received length of the current data; |
|  | Total input length: The total length of the data frame; |
| Data In 0~ Data In 31 | Receive data buffer. |

Output parameter description:

| Meaning of Ctrl Control words | Transmit request: send request; |
| --- | --- |
|  | Receive accepted: data received; |
|  | Init request: reinitialize the serial port; |
|  | Put data: write the send data to the send buffer; |
|  | Output length: the total length of the send data frame; |
| Data Out 0~ Data Out 31 | Send data buffer. |

When conducting free port communication, it is recommended to initialize the serial port before receiving or sending data. After the serial port is successfully initialized, the initialization control word "Init request" needs to be set to 0. Otherwise, the serial port will not be able to receive and send data normally.

Send data:

- Initialize the serial port, set the COM1 control word "Init request" to 1. The initialization is completed when the COM1 status word "Initaccepted" shows 1.

- Set the transmission data length by writing 40 to the COM1 control word "Output length".

- Write the data from 1 to 32 into Output1 to Output32 in sequence (only a maximum of 32 bytes of data can be written to the transmission buffer at a time. If the length of the data to be sent is greater than 32 bytes, the data needs to be written to the transmission buffer in batches and then sent out at one time. For example, when sending 40 bytes of data, write them to the transmission buffer in two batches and then send out the 40 bytes at one time).

- Set the COM1 control word "Transmit request" to 1 and at the same time set the control word "Put data" to 1.

- Read the COM1 status word "PutData Done". When "PutData Done" is 1, the 32 bytes have been successfully written to the transmission buffer, and then set the control word "Put data" to 0.

(6) Write the data from 33 to 40 into Output1 to Output8, and then set the control word "Put data" to 1.

(7) When the COM1 status word "Transmit Done" is 1, the current data frame is sent successfully, and set the control words "Transmit request" and "Put data" to 0; the sending of the current frame is completed.

Receive data:

- When the module is receiving data, the COM2 status word "Receive request" is 1, and "Input length" being 32 indicates that the currently receivable data is 32, and the "Total input length" shows a total length of 40.

(2) Read Input1 to Input 32 to read the first 32 bytes, and set the COM2 control word "Receive accepted" to 1. When the COM2 status word "Receive request" is read as 0 at this time, set the COM2 control word "Receive accepted" to 0. After it is set to 0, the COM2 status word "Receive request" shows 1, and "Input length" shows 8, indicating that there are 8 bytes of data to be received.

(3) At this time, read Input1 to Input 8 to read the last 8 bytes. After reading, set the COM2 control word "Receive accepted" to 1 and then to 0. After it is set to 0, the COM1 status word "Receive request" shows 1. The reception of the current data frame is completed.

- High-speed Counting Module

SRE5012/SRE5034 High-performance High-speed Counting Modules, with 2/4-channel counting input, support for 4-channel latching function, and support for ordinary counting function.

  - Electrical Specifications

| Model | SRE5012 | SRE5034 |
| --- | --- | --- |
| Technical specifications |  |  |
| High-speed counting channel | 2 channels (A, B, C) single-ended input maximum 200KHZ (Supports rated voltage 5VDC, 24VDC); differential maximum 4MHZ, rated voltage 5VDC | 4 channels (A, B, C), differential max. 4MHZ, rated voltage 5VDC |
| Bus 5VDC current consumption | 200mA | 200mA |
| High-speed counter input characteristics | Single-ended (rated 24V maximum 200KHZ), differential (5V maximum 4MHZ) | Differential (5V max 4MHZ) |
| Latch input characteristics | Single-ended input, 24V |  |
| Gating signal output | 2DO, NPN | 4DO, NPN |
| Distributed clock | Support |  |
| Isolation |  |  |
| Between channels and buses | Yes |  |
| Display indication | Power supply green LED display |  |
| System power diagnostics and warnings | Support |  |
| Operating environment | Operating temperature: - 20~60℃; relative humidity: 5%~90% (no condensation) |  |
| Dimensions (length x width x height) | 30×80×100（mm） | 30×80×100（mm） |

  - 14.2. Wiring Diagram

    - 14.2.1. SRE5012 Wiring Diagram

Note: Q1~Q2 are NPN output channels. The wiring example in the figure only represents differential and single-ended connections, and it does not mean that each channel can only be limited to the connection methods shown in the figure.

    - 14.2.2. SRE5034 Wiring Diagram

Note: L1, L2, L3, and L4 are 24V single-ended input channels, and Q1~Q4 are NPN output channels. The wiring example in the figure only represents differential and single-ended connection methods, and it does not mean that each channel can only be limited to the connection methods shown in the figure.

  - 14.3. Indicator Description

    - 14.3.1. SRE5012 Indicator Description

| Indicator | Description |
| --- | --- |
| PWR (Green) | Module Power Indicator: Bright: The power supply is normal Off: The power supply is abnormal |
| 5V (Green) | 5V Power Output Indicator: Bright: The power output is normal OFF: The power output is abnormal |
| Q1 (Green) | On: Channel 1 gated output. Off: Channel 1 gated output is not available. |
| Q2 (Green) | On: Channel 2 gated output. Off: Channel 2 gated output is not available. |
| Al | Channel 1, A phase input indication |
| B1 | Channel 1, B phase input indication |
| C1 | Channel 1, C phase input indication |
| A2 | Channel 2, A phase input indication |
| B2 | Channel 2, B phase input indication |
| C2 | Channel 2, C phase input indication |
| L1 | L1 input indication |
| L2 | L2 input indication |
| L3 | L3 input indication |
| L4 | L4 input indication |

    - 14.3.2. SRE5034 Indicator Description

| Indicator | Description |
| --- | --- |
| PWR (Green) | Module Power Indicator: Bright: The power supply is normal Off: The power supply is abnormal |
| 5V (Green) | 5V Power Output Indicator: Bright: The power output is normal OFF: The power output is abnormal |
| Q1 (Green) | On: Channel 1 gate control has output. Off: Channel 1 gate control has no output. |
| Q2 (Green) | On: Channel 2 gate control has output. Off: Channel 2 gate control has no output. |
| Q3 (Green) | On: Channel 3 gate control has output. Off: Channel 3 gate control has no output. |
| Q4 (Green) | On: Channel 4 gate control has output. Off: Channel 4 gate control has no output. |
| Al | Channel 1, A phase input indication |
| B1 | Channel 1, B phase input indication |
| C1 | Channel 1, C phase input indication |
| A2 | Channel 2, A phase input indication |
| B2 | Channel 2, B phase input indication |
| C2 | Channel 2, C phase input indication |
| A3 | Channel 3, A phase input indication |
| B3 | Channel 3, B phase input indication |
| C3 | Channel 3, C phase input indication |
| A4 | Channel 4, A phase input indication |
| B4 | Channel 4, B phase input indication |
| C4 | Channel 4, C phase input indication |
| L1 | L1 input indication |
| L2 | L2 input indication |
| L3 | L3 input indication |
| L4 | L4 input indication |

  - 14.4. Module Terminal Description

    - 14.4.1. SRE5012 Terminal Description

| Terminal | Description |
| --- | --- |
| A1+/A1- | Channel 1, A phase input terminal |
| B1+/B1- | Channel 1, B phase input terminal |
| C1+/C1- | Channel 1, C phase input terminal |
| L1_24V/COM1 | LATCH1 input terminal |
| A2+/A2- | Channel 2, A phase input terminal |
| B2+/B2- | Channel 2, B phase input terminal |
| C2+/C2- | Channel 2, C phase input terminal |
| L2_24V/COM2 | LATCH2 input |
| A1 | Channel 1, A phase input terminal |
| B1 | Channel 1, B phase input terminal |
| C1 | Channel 1, C phase input terminal |
| COM3 | Channel 1 A, B, C phase input common terminal COM |
| A2 | Channel 2, A phase input terminal |
| B2 | Channel 2, B phase input terminal |
| C2 | Channel 2, C phase input terminal |
| COM4 | Channel 2 A, B, C phase input common terminal COM |
| L_24V/COM5 | LATCH3 input terminal |
| L_24V/COM6 | LATCH4 input terminal |
| Q1 | Channel 1 gated output, NPN |
| Q2 | Channel 2 gated output, NPN |
| 5V/0V | 5V DC power supply output terminal |

    - 14.4.2. SRE5034 Terminal Description

| Terminal | Description |
| --- | --- |
| A1+/A1- | Channel 1, A phase differential input terminal |
| B1+/B1- | Channel 1, B phase differential input terminal |
| C1+/C1- | Channel 1, C phase differential input terminal |
| A2+/A2- | Channel 2, A phase differential input terminal |
| B2+/B2- | Channel 2, B phase differential input terminal |
| C2+/C2- | Channel 2, C phase differential input terminal |
| A3+/A3- | Channel 3, A phase differential input terminal |
| B3+/B3- | Channel 3, B phase differential input terminal |
| C3+/C3- | Channel 3, C phase differential input terminal |
| A4+/A4- | Channel 4, A phase differential input terminal |
| B4+/B4- | Channel 4, B phase differential input terminal |
| C4+/C4- | Channel 4, C phase differential input terminal |
| L1_24V | LATCH1 input terminal |
| L2_24V | LATCH2 input terminal |
| L3_24V | LATCH3 input terminal |
| L4_24V | LATCH4 input terminal |
| COM | LATCH input common terminal COM |
| 5V/0V | 5V DC power supply output terminal |
| Q1 | Channel 1 gated output, NPN |
| Q2 | Channel 2 gated output, NPN |
| Q3 | Channel 3 gated output, NPN |
| Q4 | Channel 4 gated output, NPN |

  - 14.5. RXPDO Parameter Description

| Input parameters | Data type | Description |
| --- | --- | --- |
| CHx |  |  |
| Counter value | UDINT | Current count value, with the highest bit being a sign bit (actually signed data) |
| C Latch value | UDINT | According to the configuration, the current count value latched in phase C |
| CHx Status |  |  |
| input A | BOOL | A phase input |
| input B | BOOL | B phase input |
| input C | BOOL | C phase input |
| Counter overflow | BOOL | 1: The current counter value has an overflow. 0: After the counter value overflows, when continuing to count upwards, the counter value exceeds 5000. |
| Counter underflow | BOOL | 1: The current counter value has an underflow. 0: After the counter value underflows, when continuing to count downwards, the counter value exceeds 5000. |
| Set counter done | BOOL | 1: Effectively set the current counter value of the counter. 0: "Set counter" is 0. |
| Latch C valid | BOOL | 1: The latch flag bit for phase C input; 0: No latching has been carried out. |
| Other |  |  |
| Latch1 | BOOL | 1: There is signal input in the Latch1 channel; 0: There is no signal input in the Latch1 channel. |
| Latch1 valid | BOOL | 1: The successful latching flag bit of the Latch1 signal; 0: No latching has been performed. |
| Latch1 value | UDINT | According to configuration, the current counter value latched by the Latch1 signal. |
| Latch2 | BOOL | 1: There is signal input in the Latch2 channel; 0: There is no signal input in the Latch2 channel. |
| Latch2 valid | BOOL | 1: The successful latching flag bit of the Latch2 signal; 0: No latching has been carried out. |
| Latch2 value | UDINT | According to the configuration, the current counter value latched by the Latch2 signal. |
| Latch3 | BOOL | 1: There is signal input in the Latch3 channel; 0: There is no signal input in the Latch3 channel. |
| Latch3 valid | BOOL | 1: The successful latching flag bit of the Latch3 signal; 0: No latching has been carried out. |
| Latch3 value | UDINT | According to the configuration, the current counter value latched by the Latch3 signal. |
| Latch4 | BOOL | 1: There is signal input in the Latch4 channel; 0: There is no signal input in the Latch4 channel. |
| Latch4 valid | BOOL | 1: The successful latching flag bit of the Latch4 signal; 0: No latching has been carried out. |
| Latch4 value | UDINT | According to the configuration, the current counter value latched by the Latch4 signal. |

  - 14.6. TXPDO Parameter Description

| Parameter | Data type | Description |
| --- | --- | --- |
| CHx |  |  |
| Set counter value | UDINT | The setting value of current counter value |
| ConfigData | BYTE | Bit0~Bit7 set the module working mode configuration |
| Set counter | BIT | Rising edge set “Set counter value” to the Current counter value Counter value |
| Enable latch C | BIT | 1: Latch the "Counter value" to the "Latch value" on the rising edge of the phase C input. Note that the latching is only carried out once. If you need to start the latching again, you need to set this parameter to 0 and then set it to 1 again (to avoid invalid and abnormal latching caused by interference). |
| Clear cnt val | BIT | Clear channel count value |
| Clear flow flag | BIT | Clear channel overflow and underflow flags |
| Gate threshold0 | UDINT | Gate comparison value 0 |
| Gate threshold1 | UDINT | Gate comparison value 1 |
| Latchx Ctrl |  |  |
| ConfigData | BYTE | Latch mode configuration |
| Enable latch extern on positive edge | BIT | 1: Latch the "Counter value" to the "Latch value" on the rising edge of the Latch. Note that the latching operation is only performed once. If you need to initiate the latching again, you should set this parameter to 0 and then reset it to 1 (to prevent invalid and abnormal latching caused by interference). |
| Enable latch extern on negative edge | BIT | 1: Latch the "Counter value" to the "Latch value" on the falling edge of the Latch. Note that the latching is only carried out once. If it is necessary to start the latching again, this parameter needs to be set to 0 and then set to 1 again (to avoid invalid and abnormal latching caused by interference). |

  - 14.7. Parameter Configuration Instructions (Channels)

    - 14.7.1. SRE5012

| Operating Mode |  |  |  |  |
| --- | --- | --- | --- | --- |
| Bit Operating Mode | Bit1 |  | Bit0 |  |
| AB phase quadrature 4 octave counting | 0 |  | 0 |  |
| AB phase quadrature single octave counting | 0 |  | 1 |  |
| Pulse + Direction Counting (A: Pulse, B: Direction. Subtract count when B is at high level, and add count when B is at low level) | 1 |  | 0 |  |
| Operating signal |  |  |  |  |
| Bit Operating Mode | Bit3 |  | Bit2 |  |
| 5V | 0 |  | 0 |  |
| 24V | 0 |  | 1 |  |
| Gated Output Configuration |  |  |  |  |
| Bit Gated Mode | Bit6 | Bit5 |  | Bit4 |
| Gated output mode 1 | 0 | 0 |  | 1 |
| Gated output mode 2 | 0 | 1 |  | 1 |
| Gated output mode 3 | 1 | 0 |  | 1 |
| Gated output mode 4 | 1 | 1 |  | 1 |
| Filter Configuration |  |  |  |  |
| Bit Filter Configuration | Bit7 |  |  |  |
| Turn off filtering | 0 |  |  |  |
| Turn on filtering | 1 |  |  |  |

    - 14.7.2. SRE5034

| Operating Mode |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Bit Operating Mode | Bit3 | Bit2 |  | Bit1 |  | Bit0 |
| AB phase quadrature 4 octave counting | --- | --- |  | 0 |  | 0 |
| AB phase quadrature single octave counting | --- | --- |  | 0 |  | 1 |
| Pulse + Direction Counting (A: Pulse, B: Direction. Subtract count when B is at high level, and add count when B is at low level) | --- | --- |  | 1 |  | 0 |
| Gated Output Configuration |  |  |  |  |  |  |
| Bit Gated Mode | Bit6 |  | Bit5 |  | Bit4 |  |
| Gated output mode 1 | 0 |  | 0 |  | 1 |  |
| Gated output mode 2 | 0 |  | 1 |  | 1 |  |
| Gated output mode 3 | 1 |  | 0 |  | 1 |  |
| Gated output mode 4 | 1 |  | 1 |  | 1 |  |
| Filter Configuration |  |  |  |  |  |  |
| Bit Filter Configuration | Bit7 |  |  |  |  |  |
| Turn off filtering | 0 |  |  |  |  |  |
| Turn on filtering | 1 |  |  |  |  |  |

  - 14.8. Parameter Configuration Description (Latch)

The parameters of SRE5012 are the same as those of SRE5034. The following takes SRE5034 as an example. SRE5012 can refer to the following parameter configuration. The ConfigData in the Latch channel is used to set the channel latching parameters:

    - 14.8.1. SRE5012

| Latch Mode Configuration |  |  |  |  |
| --- | --- | --- | --- | --- |
| Bit Value | Bit3 | Bit2 | Bit1 | Bit0 |
| Latch channel latches count channel 1 | --- | --- | --- | 0 |
| Latch channel latches count channel 2 | --- | --- | --- | 1 |

    - 14.8.2. SRE5034

| Latch Mode Configuration |  |  |  |  |
| --- | --- | --- | --- | --- |
| Bit Value | Bit3 | Bit2 | Bit1 | Bit0 |
| Latch channel latches counting channel 1 | --- | --- | --- | 0 |
| Latch channel latches counting channel 2 | --- | --- | --- | 1 |
| Latch channel latches counting channel 3 | --- | --- | 1 | 0 |
| Latch channel latches counting channel 4 | --- | --- | 1 | 1 |

| Parameter | Data type | Description |
| --- | --- | --- |
| Latchx Ctrl |  |  |
| ConfigData | BYTE | Latch mode configuration |
| Enable latch extern on positive edge | BIT | 1: Latch the "Counter value" to the "Latch value" on the rising edge of the Latch. Note that the latching is only performed once. If it is necessary to start the latching operation again, this parameter should be set to 0 and then set back to 1 (to avoid invalid and abnormal latching caused by interference). |
| Enable latch extern on negative edge | BIT | 1: Latch the "Counter value" into the "Latch value" on the falling edge of the Latch signal. Note that the latching operation is only carried out once. If you need to initiate the latching again, you should set this parameter to 0 and then reset it to 1 (to prevent invalid and abnormal latching caused by interference). |

  - 14.9. Gated Output Mode Description

    - 14.9.1. Gated Output Mode 1

Compare the comparison value and the upper limit of the counter:

When the gating comparison value 0 < counter value < the upper limit of the counter (i.e., 232-1): The gating (i.e., the Q channel) will output.

When the lower limit of the counter (i.e., 0) < counter value < the gating comparison value 0: The gating (i.e., the Q channel) will not output.

Note: The value of the gating comparison value 1 must be greater than the gating comparison value 0, otherwise the output will be abnormal.

    - 14.9.2. Gated Output Mode 2

Compare the comparison values and the upper limit of the counter:

When the gating comparison value 0 < the counter value < the upper limit of the counter (i.e., 232-1): the gating (that is, the Q channel) will not output.

When the lower limit of the counter (i.e., 0) < the counter value < the gating comparison value 0, the gating (that is, the Q channel) will output.

Note: The value of the gating comparison value 1 must be set to be greater than that of the gating comparison value 0. Otherwise, the output will be abnormal.

    - 14.9.3. Gated Output Mode 3

Compare between the comparison value 0 and the comparison value 1:

When the gating comparison value 0 < the counter value < the gating comparison value 1, the gating (that is, the Q channel) will output.

When the lower limit of the counter (i.e., 0) < the counter value < the gating comparison value 0, or the gating comparison value 1 < the counter value < the upper limit value (i.e., 232-1), the gating (that is, the Q channel) will not output.

Note: The value set for the gating comparison value 1 must be greater than that of the gating comparison value 0. Otherwise, there will be abnormal output.

    - 14.9.4. Gated Output Mode 4

Compare the comparison value 0 and the comparison value 1:

When the gating comparison value 0 < the counter value < the gating comparison value 1, the gating (i.e., the Q channel) will not output.

When the lower limit of the counter (i.e., 0) < the counter value < the gating comparison value 0, or the gating comparison value 1 < the counter value < the upper limit value (i.e., 232-1), the gating (i.e., the Q channel) will output.

Note: The value of the gating comparison value 1 must be set to be greater than that of the gating comparison value 0. Otherwise, there will be abnormal output.

- High-speed pulse output module SRE5234

4-axis PTO output, NPN type output, single-ended up to 400KHZ, differential output up to 1MHZ, configurable parameters via XML file.

  - Electrical Specifications

| Model | SRE5234 |
| --- | --- |
| Technical specifications |  |
| High-speed pulse output channel | 4 channels |
| Bus 5VDC current consumption | 165.5mA |
| Signal output | NPN type output |
|  | Differential 5V, 1MHz max |
|  | Single-ended, 24V max 200KHz or 5V max 400KHz |
| Signal type | Pulse + Direction |
| Isolation |  |
| Between channels and buses | Yes |
| Display indication | Power supply green LED display |
| System power diagnostics and warnings | support |
| Operating environment | Operating temperature: -20~60℃, relative humidity: 5%~90% (no condensation) |
| Dimensions (length× width × height) | 30×80×100(mm) |

  - Electrical Wiring Diagram

Driver

Driver

- Differential output supports only 5VDC.

- Single-ended support allows for both 24VDC and 5VDC.

Single-ended connection

Differential wiring

  - Indicator Description

| Terminal | Terminal description |
| --- | --- |
| P1+ | Axis 1 differential output, pulsed positive signal |
| P1- | Axis 1 differential output, negative pulse signal |
| D1+ | Axis 1 differential output, directional positive signal |
| D1- | Axis 1 differential output, negative direction signal |
| P2+ | Axis 2 differential output, positive pulse signal |
| P2- | Axis 2 differential output, negative pulse signal |
| D2+ | Axis 2 differential outputs, positive direction signals |
| D2- | Axis 2 differential outputs, negative direction signals |
| P3+ | Axis 3 differential output, positive pulse signal |
| P3- | Axis 3 differential output, negative pulse signal |
| D3+ | Axis 3 differential outputs, positive direction signals |
| D3- | Axis 3 differential outputs, negative direction signals |
| P4+ | Axis 4 differential output, positive pulse signal |
| P4- | Axis 4 differential output, negative pulse signal |
| D4+ | Axis 4 differential outputs, positive direction signals |
| D4- | Axis 4 differential output, negative direction signal |
| P1 | Axis 1 single-ended output, pulse signal |
| D1 | Axis 1 single-ended output, directional signals |
| P2 | Axis 2 single-ended output, pulse signal |
| D2 | Axis 2 single-ended output, directional signals |
| P3 | Axis 3 single ended output, pulse signal |
| D3 | Axis 3 single-ended output, directional signals |
| P4 | Axis 4 single-ended output, pulse signal |
| D4 | Axis 4 single-ended output, directional signal |
| M | Single-ended output common |

  - Indicator Description

| Indicator | Description |
| --- | --- |
| PWR (Green) | Module power indicator: On: The module power supply is normal; Off: The module is powered off; |
| RUN (Green) | Communication indicator: On: Communication is normal Off: Communication is abnormal |
| P1 | Axis 1 pulse output, when there is a signal, the indicator light is on, otherwise it is off. |
| P2 | Axis 2 pulse output, when there is a signal, the indicator light is on, otherwise it is off. |
| P3 | Axis 3 pulse output, when there is a signal, the indicator light is on, otherwise it is off. |
| P4 | Axis 4 pulse output, when there is a signal, the indicator light is on, otherwise it is off. |
| D1 | Axis 1 direction output, when there is a signal, the indicator light is on, otherwise it will be off. |
| D2 | Axis 2 direction output, when there is a signal, the indicator light is on, otherwise it is off. |
| D3 | Axis 3 direction output, when there is a signal, the indicator light is on, otherwise it will be off. |
| D4 | Axis 4 direction output, when there is a signal, the indicator light is on, otherwise it will be off. |

  - COE Parameter Description

| Parameter | Data type | Description |
| --- | --- | --- |
| 2004:01 | Err 24v_nf | Bit0: 1: Channel 24V power supply is abnormal; 0: Normal. |

  - PDO Parameter Description

| Item | Sub-item | Data type | Description |
| --- | --- | --- | --- |
| Axis（1-4） Input | M_Status | Byte | The status of the module. M_Status[6:0]: 000_0000: The module is idle 000_0010: The module is running; 000_0110: Module software emergency stop status; 000_1000: The pulse transmission completion status of the module; 1xx_xxxx: Start running flag. M_Status [6]: The module starts to run the flag bit, the M_ctrl is set from 0 to 1, the flag signal is set to 1, and only the bit6 of the controller Mctrl writes 1 to clear the flag signal. M_Status[7]: 0: Invalid 1: After the Mctrl RUN command is reset, when the flag is detected as 1, the Mctrl RUN command is set, and the module starts the pulse output |
|  | M_Pos_Relative | DINT | Run relative position. |
|  | M_Spd | UDINT | The current speed of the module. |
|  | M_ERROR | Byte | 0: Normal Bit0: The starting speed is greater than the running speed. Bit2: Mode error |
| Axis（1-4） Output | M_Ctrl | Byte | BIT0: RUN, command run enabled, rising edge, run, falling edge, stop. BIT1: UPDATE, set 1 to be valid, update the operating parameters (AccTime, DecTime, Spdss, Spdset, Posset parameters) during the motor operation. BIT2: ESTOP, the command stops urgently, the module receives the command, and immediately stops the pulse output, without acceleration or deceleration in the middle. The default value is 0, when an emergency stop is required, the position is 1, and the position should be reset to 0 before the next run BIT3: Retention; BIT4: Alarm clearing. BIT5: Speed mode direction bit, speed mode, control direction forward or reverse. BIT6: The running flag is cleared, the module is finished, the M_Status [6] will be set, the PLC detects that the flag signal is 1 (closed-loop detection), then the module successfully sends a pulse, and the next time it needs to send a pulse, the operation flag is cleared through the clearing instruction, and the next operation detection is started. BIT7: Retention; |
|  | Work_Mode | Byte | 0: Relative position output mode 1: Speed mode Other: Relative position mode Note: To change WorkMode, M_Ctrl=0. |
|  | AccTime | UINT | Acceleration time (ms). To set acceleration |
|  | DecTime | UINT | Deceleration time (ms). To set deceleration |
|  | SpdSs | UDINT | User-set start speed or stop speed (Hz), the data range is 0~4000000 |
|  | SpdSet | UDINT | User-set running speed (Hz), the data range is 0~4000000 |
|  | PosSet | DINT | User-set position, in the number of pulses. |

- Usage Example

  - SRE8200 Coupler and Communication Instructions with BECKHOFF Main Station

    - Communication Connection

Communication connection diagram is as shown followings:

    - Hardware Configuration

The hardware configuration is shown in the following table:

| Hardware | Quantity | Notes |
| --- | --- | --- |
| Programming computer | 1 unit | Install TwinCAT3 software |
| SRE8200 | 1 piece | EtherCAT communication coupler |
| SRE1116 | 1 piece | Digital input module |
| SRE2116 | 1 piece | Digital output module |
| SRE3204 | 1 piece | Analog input module |
| SRE4204 | 1 piece | Analog output module |
| Network cable | Some |  |
| 24V Switching Power Supply | 1 piece |  |

    - Install XML Files

Install XML files into TwinCAT3, the default folder in the example is

“C:\TwinCAT\3.1\Config\Io\EtherCAT” as shown in the following figure:

    - New Project and Configuration

Open TwinCAT3 software and create a new project as shown in the following figure:

Scan SRE8200 and its extended IO connected to the computer into the project, click I/O>Devices>Scan, as shown in the following figure:

The successfully scanned module is shown in the following figure:

    - Data Monitoring

Select the IO module to be monitored on TwinCAT3 and choose the data to be monitored:

Digital input/output:

Analog input/output:

  - Example of Communication between SRE2116 and TwinCAT3

This example introduces the connection of SRE8200 coupler to SRE2116 and SRE1016, and the monitoring of the data through Beckhoff. The connection and usage of digital inputs and digital outputs can refer to this example.

    - Communication Connection

Communication connection diagram is shown as follows:

    - Hardware Configuration

The hardware configuration is shown in the following table:

| Hardware | Quantity | Notes |
| --- | --- | --- |
| Programming computer | 1 unit | Install TwinCAT3 software |
| SRE8200 | 1 piece | EtherCAT communication coupler |
| SRE2116 | 1 piece | High performance digital output module |
| SRE1116 | 1 piece | High performance digital input module |
| Network cable | 1 item |  |
| 24V Switching Power Supply | 1 piece |  |

    - Install XML Files

Install XML files into TwinCAT3, the default folder in the example is

“C:\TwinCAT\3.1\Config\Io\EtherCAT”, as shown in the following figure:

    - New Project and Configuration

Open TwinCAT3 software and create a new project as shown in the following figure:

Scan the ECT coupler SRE8200 and its extended IO connected to the computer into the project, click I/O>Devices>Scan, as shown in the following figure:

The successfully scanned module is shown in the following figure:

    - Data Monitoring

Select the IO module to be monitored on TwinCAT3 and choose the data to be monitored:

  - SRE3204 Communication Example

    - Example of Communication with TwinCAT3

This example introduces the connection of SRE8200 coupler to SRE3204 and SRE4204, and the monitoring of the data through Beckhoff. The connection and usage of analog inputs and analog outputs can refer to this example.

      - Communication Connection

Communication connection diagram, as shown in the following figure:

Programming computer

TwinCAT3

      - Hardware Configuration

The hardware configuration is shown in the following table:

| Hardware | Quantity | Notes |
| --- | --- | --- |
| Programming computer | 1 unit | Install TwinCAT3 software |
| SRE8200 | 1 piece | EtherCAT communication coupler |
| SRE3204 | 1 piece | High performance analog input module |
| SRE4204 | 1 piece | High performance analog output module |
| Network cable | 1 item |  |
| 24V switching power supply | 1 piece |  |

      - Install XML Files

Install XML files into TwinCAT3, the default folder in the example is

“C:\TwinCAT\3.1\Config\Io\EtherCAT”, as shown in the following figure:

      - New Project and Configuration

Open TwinCAT3 software and create a new project as shown in the following figure:

Scan SRE8200 and its extended IO connected to the computer into the project, click on I/O>Devices>Scan, as shown in the following figure:

The successfully scanned module is shown in the following figure:

      - Data Monitoring

Select the IO module to be monitored on TwinCAT3 and choose the data to be monitored:

    - Example of Communication with Omron

This example introduces the connection of SRE8200 coupler to SRE3204 and SRE4204, and the monitoring of the data through Omron. The connection and usage of analog input and analog output modules can refer to this example.

      - Communication Connection

Communication Connection schematic, as shown in the following figure:

Programming computer

Sysmac Studio

      - Hardware Configuration

The hardware configuration is shown in the following table:

| Hardware | Quantity | Notes |
| --- | --- | --- |
| Programming computer | 1 unit | Install Sysmac Studio software |
| SRE8200 | 1 piece | EtherCAT communication coupler |
| SRE3204 | 1 piece | High-performance analog input module |
| SRE4204 | 1 piece | High-performance analog output module |
| Network cable | 1 piece |  |
| 24V switching power supply | 1 piece |  |

      - New Project Installation XML File

- Create a new project and select the CPU model to be used. In this example, the NX1P2-9024DT CPU model is applied.

- After creating a new blank project, install XML files.

- After the installation is completed, pull down the list to view the installed XML files.

      - Configuration Engineering

- Establish connection between programming computer and Omron controller. In this example, the IP address of Omron controller is 192.168.250.1, and the IP address of programming computer is 192.168.250.111. Test whether the communication between the programming computer and Omron controller is normal, as shown in the following figure:

- After the communication between the programming computer and the controller is normal, set the controller to the online state, and scan the coupler and the connected expansion modules onto the Sysmac Studio.

- After the scanning is successful, transfer the data to CPU.

      - Data Monitoring

- Click on I/O mapping to perform Data Monitoring on the connected modules.

  - Example of Communication between SRE3522 and TwinCAT3

    - Communication Connection

As shown in the following figure:

Programming computer

    - Hardware Configuration

The hardware configuration is shown in the following table:

| Hardware | Quantity | Notes |
| --- | --- | --- |
| Programming computer | 1 unit | Install TwinCAT3 software |
| SRE8200 | 1 piece | EtherCAT communication coupler |
| SRE3522 | 1 piece | Analog fast acquisition module |
| Signal generator | 1 piece |  |
| Network cable | 1 piece |  |
| 24V Switching Power Supply | 1 piece |  |

    - Install XML Files

Install XML files into TwinCAT3, the default folder in the example is

“C:\TwinCAT\3.1\Config\Io\EtherCAT”, as shown in the following figure:

    - New Project and Configuration

Open TwinCAT3 software and create a new project as shown in the following figure:

Scan SRE8200 and its extended IO connected to the computer into the project, click on I/O>Devices>Scan, as shown in the following figure:

The successfully scanned module is shown in the following figure:

    - Data Monitoring

Select the IO module to be monitored on TwinCAT3 and choose the data to be monitored:

  - Example of Communication between SRE6004 and TwinCAT3

This example introduces the simple usage of SRE8200 coupler connected to SRE6004 serial port module. Data Monitoring of SRE6004 serial port module is carried out through Beckhoff. It enables data interaction of SRE6004 in the master station, slave station, and free port modes. The connection of SRE6002 can refer to this example.

    - Communication Connection

Schematic diagram of Communication Connection, as shown in the following figure:

Programming computer

    - Hardware Configuration

The hardware configuration is shown in the following table:

| Hardware | Quantity | Notes |
| --- | --- | --- |
| Programming computer | 1 unit | Install TwinCAT3 software |
| SRE8200 | 1 piece | EtherCAT communication coupler |
| SRE6004 | 1 piece | High-performance serial port module |
| Network cable | 1 piece |  |
| 24V switching power supply | 1 piece |  |

    - Install XML Files

Install XML files into TwinCAT3, the default folder in the example is

“C:\TwinCAT\3.1\Config\Io\EtherCAT”, as shown in the following figure:

    - New Project and Configuration

Open TwinCAT3 software and create a new project as shown in the following figure:

Scan SRE8200 connected to the computer and the connected serial port module SRE6004 into the project. Click on I/O > Devices > Scan, as shown in the following figure:

The successfully scanned module is shown in the following figure:

    - Modbus RTU Communication of SRE6004

This example uses Modbus RTU communication between COM1 and COM3 on SRE6004 for illustration, and it is carried out in RS232 connection mode. COM1 is set as the Modbus RTU master station, and COM3 is set as the slave station. The interaction data is as follows:

- Add the relevant configurations of COM1 master station and COM3 slave station.

- Configure COM1 as Modbus RTU master station, and add the master station parameter configuration as shown in the following figure:

- Configure COM3 as a Modbus RTU slave station. Determine the read and write addresses of the slave station according to the added number of read and write bytes. The data area where the slave station module allows the master station to perform read operations is 40001~ 40017; the data area where the master station is allowed to perform write operations is 40257~40273. The parameter configuration is shown in the following figure:

- After the configuration is completed, click "Refresh IO", and then check whether the status of the module is in the "OP" state. If it is in the "OP" state, the configuration is correct; otherwise, the configuration is incorrect.

- Configure the communication parameters of COM1 and COM3. The parameter configurations should be the same; otherwise, normal communication will not be possible. As shown in the following figure:

- Configure the station address of COM3 slave station.

- Set COM1 master station to access the data of COM3 slave station.

- After configuring COM1 communication parameters, check the module status. A status display of 1 indicates that the communication is normal and data can be sent normally.

- After the above configurations are completed, data sending and receiving can be carried out.

    - SRE6004 Free Port Communication

This example illustrates the free port communication between COM1 and COM2 on SRE6004. It uses RS232 connection method, where COM1 sends data and COM2 receives data. The interaction data is as follows:

- Configure COM1 and COM2 to free port mode. The parameter configuration is shown in the following figure:

After the configuration is completed, click "Refresh IO", and then check whether the status of the module is in the "OP" state. If it is in the "OP" state, the configuration is correct; otherwise, the configuration is incorrect.

- Configure the communication parameters of COM1 and COM2. When COM1 and COM2 perform free port communication, the baud rate, parity, and stop bits of the communication parameters need to be set consistently, otherwise normal communication will not be possible, as shown in the following figure:

- Data Monitoring

Note: When performing free port communication, it is recommended to initialize the serial port before receiving or sending data. After the serial port is initialized successfully, the initialization control word “Init request” needs to be set to 0, otherwise the serial port cannot send and receive data normally.

Send data:

- Initialize the serial port. Set COM1 control word “Init request” to 1. When COM1 status word “Init accepted” is displayed 1, the initialization is completed.

- Set the data sending length. Write 40 into the COM1 control word “Output length”.

- Write the data 1~32 to be sent into “Data Out 0-Data Out 31” in sequence. (Each time, a maximum of 32 bytes of data can be written into the sending buffer. If the length of the data to be sent is greater than 32 bytes, the data needs to be written into the sending buffer in batches, and then the data is sent out at one time. For example, when sending 40 bytes of data, write it into the sending buffer in 2 batches, and then send out the 40 bytes at one time)

- Set the COM1 control word “Transmit request” to 1, and at the same time, set the control word “Put data” to 1.

- Read the COM1 status word “PutData Done”. When “PutData Done” is 1, 32 bytes have been successfully written into the sending buffer, and set the control word “Put data” to 0.

- Write 33~40 into “Data Out 0-Data Out 7” in sequence, and then set the control word “Put data” to 1.

- When the COM1 status word “Transmit Done” is 1, the current data frame has been sent successfully, and set the control word “Transmit request” and “Put data” to 0 to complete the sending of the current frame.

Receive data:

- When the module receives data, the COM2 status word “Receive request” is 1, and when “Input length” is 32, it indicates that 32 bytes of data can be received currently. The “Total input length” shows a total length of 40.

- Reading “Data In 0 - Data In 31” allows you to read the first 32 bytes. Set the COM2 control word “Receive accepted” to 1. When the COM2 status word “Receive request” is read as 0 at this time, set the COM1 control word “Receive accepted” to 0. After setting it to 0, the COM1 status word “Receive request” is displayed as 1, and “Input length” is displayed as 8, indicating that 8 bytes of data are to be received.

- At this time, reading “Data In 0 - Data In 7” allows you to read the last 8 bytes. After reading, set the COM1 control word “Receive accepted” to 1. When the COM1 status word “Receive request” is read as 0 at this time, set the COM2 control word “Receive accepted” to 0. After setting it to 0, the COM1 status word “Receive request” is displayed as 0, and the reception of the current data frame is completed.

    - SRE6004 as Modbus Slave

- Set COM1 as a slave

- Configure COM1 slave communication parameters

- Configure the communication parameters of the ModbusMaster master station. They need to be the same as those of the COM1 slave station. Otherwise, communication will fail.

- Set slave ID

- Data interaction, data is shown in the figure, the master station reads the data of SRE6004 40001~40017 address: the master station writes the data of SRE6004 40257~40273 address:

  - Example of Communication between SRE5034 and TwinCAT3

This example introduces the usage of SRE5034 module behind SRE8200 coupler. The connection of SRE5012 can refer to this example. The operation process is as follows:

    - Communication Connection

Schematic diagram of Communication Connection, as shown in the following figure:

Programming computer

TwinCAT3

    - Hardware Configuration

The hardware configuration is shown in the following table:

| Hardware | Quantity | Notes |
| --- | --- | --- |
| Programming computer | 1 unit | Install TwinCAT3 software |
| SRE8200 | 1 piece | EtherCAT communication coupler |
| SRE5034 | 1 piece | Counting module |
| Network cable | Some |  |

    - Install XML Files

Install XML files into TwinCAT3, the default folder in the example is

“C:\TwinCAT\3.1\Config\Io\EtherCAT”, as shown in the following figure:

    - New Project and Configuration

Open TwinCAT3 software and create a new project as shown in the following figure:

Scan SRE8200 and its high-speed counting module SRE5034 connected to the computer into the project, click I/O> Devices> Scan, as shown below:

The successfully scanned module is shown in the following figure:

    - Data Monitoring

Select the IO module to be monitored on TwinCAT3 and select the channel to be monitored for monitoring, as shown in the following figure:

  - Example of Communication between SRE5202 and TwinCAT3

This example demonstrates the use of SRE8200 to expand SRE5202 for communication connection. The data of SRE5202 module is monitored through Beckhoff. The connection and usage of SRE5204 can refer to this example.

    - Communication Connection

Communication connection diagram, as shown in the following figure:

Programming computer

TwinCAT3

    - Hardware Configuration

The hardware configuration is shown in the following table:

| Hardware | Quantity | Notes |
| --- | --- | --- |
| Programming computer | 1 unit | Install TwinCAT3 software |
| SRE8200 | 1 piece | EtherCAT communication coupler |
| SRE5202 | 1 piece |  |
| Network cable | 1 piece |  |
| 24V switching power supply | 1 piece |  |

    - Install XML Files

Install XML files into TwinCAT3, the default folder in the example is

“C:\TwinCAT\3.1\Config\Io\EtherCAT”, as shown in the following figure:

    - New Project and Configuration

Open TwinCAT3 software and create a new project as shown in the following figure:

Connect SRE8200 coupler to the computer, scan the extended SRE5202 module into the project, and click I/O> Devices> Scan, as shown in the following figure:

The successfully scanned module is shown in the following figure:

    - Data Monitoring

According to actual usage requirements, parameter settings for SRE5202 can be performed through the DC/Oversampling parameter setting column.

- Sampling data by Bit type:
For example: Select 2 Channels (Bits), 128Bit, that is, the process oversampling coefficient of SRE5202 channel 1 and channel 2 is 128Bit. That is, two channels are selected, and the total cycle time is 4000us. Set the channel output. According to the total cycle time and the oversampling coefficient, the sampling cycle time is 31.250us. Set the channel to 1, and the channel will continuously output according to the sampling cycle time.

- Sampling data by Byte type:

For example: Select 2 Channels (Bytes), 16 (2*8), that is, the oversampling coefficient of SRE5202 channel 1 and channel 2 is 2 Bytes (16 Bits). That is, two channels are selected. According to the total cycle time and the oversampling coefficient, the sampling cycle time is 250 us. As follows, set the first eight bits of channel 1 to 1, and the channel will continuously output according to the sampling cycle time.

Total cycle time, set by Freerun Cycle (ms).

  - Example of Communication between SRE5234 and TwinCAT3

    - Communication Connection

Communication connection diagram, as shown in the following figure:

Programming computer

TwinCAT3

    - Hardware Configuration

The hardware configuration is shown in the following table:

| Hardware | Quantity | Notes |
| --- | --- | --- |
| Programming computer | 1 unit | Install TwinCAT3 software |
| SRE8200 | 1 piece | EtherCAT communication coupler |
| SRE5234 | 1 piece |  |
| Network cable | 1 piece |  |
| 24V switching power supply | 1 piece |  |

    - Install XML Files

Install XML files into TwinCAT3, the default folder in the example is

“C:\TwinCAT\3.1\Config\Io\EtherCAT”, as shown in the following figure:

    - New Project and Configuration

Open TwinCAT3 software and create a new project as shown in the following figure:

Connect SRE8200 coupler to the computer, scan the extended SRE5234 module into the project, and click I/O> Devices> Scan, as shown in the following figure:

The successfully scanned module is shown in the following figure:

    - Data Monitoring

Select the IO module to be monitored on TwinCAT3, choose Axis 1 for monitoring, and carry out parameter configuration. After the parameter configuration is completed, the control word needs to be set to 1 to indicate the start of output. An example is shown in the following figure:

You can check the parameters through the corresponding axis in Axis Inputs and pay attention to the running status of the axis, as shown in the following figure:

- Appendix Configuration Parameter Description

  - TwinCAT3 Startup Function Description

The parameter settings of the expansion module in the COE do not have a saving function. Each time the expansion IO module is rescanned or the power is turned on again, the configuration of the expansion IO module will revert to the factory settings. When setting the parameters of the expansion IO module in the startup item, parameters are written into the coupler every time communication is established. In the same project, when the power is turned on repeatedly, the parameter configuration of the expansion module remains unchanged.

For example, the CH1-CH4 channel range of SRE4204 is configured to 0-20mA/0-10V.

After the parameter configuration is completed, it is necessary to refresh to update the data into the COE parameters. At this time, the parameters will take effect and be retained even after power outage. However, once the device is rescanned, the settings will revert to the original configuration.

Note: When configuring parameters for SRE3204/SRE3208, different parameters can only be configured under different parameter directories. For example, when you click on the first parameter directory, you set the first parameter in that directory; when you click on the second parameter directory, you set the second parameter in that directory. If the same parameter is configured under three parameter directories, it will be replaced by the last configured parameter, and the last configured parameter will be executed.

  - Codesys Startup Parameter Setting Extension Module Parameter Description

The parameters of the expansion module do not have the saving function. Every time the expansion IO module is rescanned or powered on again, the configuration of the expansion IO module will be restored to its factory settings. Set the parameters of the extended IO module in the startup item, and write the parameters to the coupler every time communication occurs. In the same project, when powered on repeatedly, the parameter configuration of the extended module remains unchanged.

Scan device, click the module where the parameters need to be modified, select the startup parameters, and view the content of the parameters that can be changed.

Click the dropdown menu to modify parameters, and the downloaded parameters will take effect after the modification is completed.

  - Description of Sysmac Studio Initialization Parameter Setting Function

The parameters of the expansion module do not have the saving function. Every time the expansion IO module is rescanned or powered on again, the configuration of the expansion IO module will be restored to its factory settings. Set the parameters of the extended IO module in the startup item, and write the parameters to the coupler every time communication occurs. In the same project, when powered on repeatedly, the parameter configuration of the extended module remains unchanged.

After scanning the device, click the module where the parameters need to be modified, and select Edit Initialization Parameter Settings.

Select parameters through the dropdown menu