## Sheet1
Reaction Stage | COD (mg/L) | Removal Rate | Reaction Stage | BOD (mg/L) | Removal Rate | Reaction Stage | TN (mg/L) | Removal Rate | Reaction Stage | TN (mg/L) | Removal Rate | Reaction Stage | Ammonia Nitrogen(mg/L) | Removal Rate
Biochemical Tank Effluent | 824.3 |  | Biochemical Tank Effluent | 416.1 |  | Biochemical Tank Effluent | 62.53 |  | Biochemical Tank Effluent | 11.4 |  | Biochemical Tank Effluent | 52.34
Anaerobic Tank Effluent | 746.5 | 9.438% | Anaerobic Tank Effluent | 406.1 | 2.403% | Anaerobic Tank Effluent | 47.898 | 23.4% | Anaerobic Tank Effluent | 12.144 |  | Anaerobic Tank Effluent | 48 | 8.292%
Anoxic Tank Effluent | 629.1 | 14.24% | Anoxic Tank Effluent | 361.4 | 10.74% | Anoxic Tank Effluent | 20.6349 | 67% | Anoxic Tank Effluent | 3.48 | 69.47% | Anoxic Tank Effluent | 33.75 | 29.69%
Aerobic Tank Effluent | 40.9 | 71.36% | Aerobic Tank Effluent | 27.6 | 80.22% | Aerobic Tank Effluent | 9.3795 | 85% | Aerobic Tank Effluent | 2.53 | 77.81% | Aerobic Tank Effluent | 3.6 | 89.33%
Water From Secondary Sedimentation Tank | 20.1 | 97.56% | Water From Secondary Sedimentation Tank | 10 | 97.6% | Water From Secondary Sedimentation Tank | 7.69 | 87.7% | Water From Secondary Sedimentation Tank | 0.3 | 97.37% | Water From Secondary Sedimentation Tank | 0.99 | 98.11%

## mbbr效率曲线
Parameter | Year | Pollution concentration [mg.dm3] | Efficiency[%] | 测定的污水中有机物去除率的平均水平为BOD(5)98.9±0.6%和COD(95.3±2.1%)，说明流出物中这些化合物的平均浓度为分别为4.3±2.1和43.3±16.7 mg02 dm3。总悬浮物去除率的平均值依次为97.6±1.5%，排放时的平均浓度为8.3±4.3 mg鿍dm3不幸的是，在分析的年份里，有十几次(约36%的结果)证明生物化合物的减少是可以实现的，低于许可证规定的水平，即TN的80.0%和TP的85.0%。事实上，在分析期间，废水中氮和磷化合物的平均去除效率分别为73.7±25.3%和87.4±10.8%。这表明处理后废水中生物源性化合物的平均浓度为25.4±24.4 mg TN dm-3和2.5±3.1 mg TP dm3原水水质评价结果表明，BOD5/TN、COD/TN、BOD5/TP和COD/TP比值均在适宜反硝化和硝化过程的推荐范围内。这就留下了与总氮去除不足有关的问题的典型原因，即低温，这被发现限制了硝化作用。此外，有可能得出结论，从污泥泻湖排出的水可能含有抑制硝化过程的物质。在磷化合物还原不足的情况下，问题是由这种污染物的额外负荷引起的。如果要提高Nowa wiezwttp中营养物去除的效率，则需要更好地组织污泥管理。可能还需要通过增加硝化室的体积或更换生物膜载体来使其适应冬季的低温。评估机械处理废水的质量也是值得的，要注意BOD/TN、COD/TN、BOD5/TP和COD/TP比率，以注意这些比率是否肯定有利于生物废水处理工艺。
minimum —— average —— maximum standard deviation —— coefficient of variation
BOD5 | 2016 | 1.8——3.4——5.5 1.3——0.38 | 98.2——99.1——99.6 0.4——0.00
| 2017 | 1.2——4.2——10.4 2.7——0.63 | 96.9——98.9——99.7 0.7——0.01
| 2018 | 1.9——5.2——7.3 1.9——0.36 | 97.7——98.7——99.7 0.6——0.01
COD | 2016 | 10.0——39.7——60.0 16.9—— 0.43 | 91.0——95.7——98.9 2.1——0.02
| 2017 | 17.0——46.9——76.0 22.2——0.47 | 90.1——94.6——98.1 2.6——0.03
| 2018 | 29.0——43.3——56.0 9.1——0.21 | 92.9 ——95.6——98.3 1.5——0.02
Total su—— spended solids 总固体悬浮物 | 2016 | 3.8——8.3——15.4 3.1——0.38 | 96.0——97.8——98.8 1.0——0.01
| 2017 | 3.0——7.6——16.8 4.2——0.55 | 91.5——97.3——98.9 2.0——0.02
| 2018 | 2.0——9.0——18.4 5.5——0.61 | 95.6——97.7——99.8 1.4——0.01
Total ni—— trogen 总氮 | 2016 | 7.52——20.8——49.7 17.8——0.85 | 41.5——78.7——91.3 17.5——0.22
| 2017 | 6.3——34.0——83.7 32.6——0.96 | 8.4——65.6——93.8 33.1——0.50
| 2018 | 7.0——21.3——59.9 19.8——0.93 | 29.9——76.7——93.1 22.9——0.30
Total pho—— sphorus 总磷 | 2016 | 0.21——2.1——9.2 2.7——1.27 | 70.0——89.4——97.3 9.7——0.11
| 2017 | 0.1——3.4——14.8 4.2——1.23 | 69.0——85.6——99.1 11.8——0.14
| 2018 | 0.32——2.1——7.31 2.0——0.95 | 56.5——87.2——97.3 11.5——0.13