## Sheet1
HANGZHOU JUNTAI PLASTIC PRODUCTS CO.LTD Head ofice : #3301, Times center, Linping ,Hangzhou, Zhejiang,China M:0086136 0051 3715 email: info@juntaiplastic.com www.juntaiplastic.com
Juntai Aeration Volume Calculator
Blue block is the design datameter : be filled in Brown: calculate process data Red : last result for your process
1.Aerobic Tank volume calculation
Calculation Formula
Design parameters:
Qmax | 150 | Daily sewage design flow, m3/d
So | 400 | Sewage untreated for five days - (BOD5 concentration), mg/l
Se | 20 | Five days after treatment - (BOD5 concentration), mg/l
BODSS | 0.12 | Sludge load, kg-BOD/kg·MLSS/day
MLSS | 4000 | Sludge concentration, mg/l
Result | 118.75 | M3
2.Denitrification cabinet volume calculation
Calculation Formula
Design parameters:
NIKN | 250 | Concentration of ammonia nitrogen in treated effluent, mg/l
NETN | 30 | Concentration of ammonia nitrogen in treated effluent, mg/l
MDNL | 0.5 | Sludge denitrification load, kg-NH3-N/kg·MLSS/day
MLSS | 3000 | Sludge concentration, mg/l
Result | 22 | M3
3.Aeration Calculation
Calculation Formula
Design parameters:
Ro2- | 172.35 | Design sewage oxygen demand, kgO2/d
So- | 400 | Five-day biochemical oxygen demand of influent water, mg/L
Se- | 20 | Five-day biochemical oxygen demand of effluent, mg/L
△Xv- | 11.0833 | Amount of microorganisms discharged from the oxidation tank to the system, kg/d
Nk- | 275 | Total Kjeldahl nitrogen in influent, mg/L
Nke- | 45 | Total Kjeldahl nitrogen in effluent, mg/L
Nt- | 275 | Total nitrogen in influent, mg/L
Noe- | 21 | Amount of nitrate nitrogen in effluent, mg/L
a- | 1.47 | Carbon equivalent, when the carbonaceous material is measured in terms of five-day biochemical oxygen demand, take 1.47
b- | 4.57 | Constant, oxygen demand for oxidizing each kilogram of ammonia nitrogen, kgO2/kgN, take 4.57.
c- | 1.42 | Constant, oxygen content of bacterial cells, taken as 1.42
d- | 0.08 | Constant, sludge auto-oxidation rate, taken as 0.08
N'- | 2.8 | Average concentration of volatile suspended solids in the mixture (g vss/L) at 70% of the sludge volume
θ- | 30 | Sludge age, 30d
Result | 172.3519 | kgO2/d
4. Absolute Pressure Calculation
Calculation Formula
Design parameters:
Pb- | 133040 | Absolute pressure at which the aeration device is located, Pa
H- | 4.3 | Aeration diffuser gas port at the water depth, m (water depth minus the aeration disc installation height, according to the depth of the tank accounting)
P- | 90900 | Atmospheric pressure, Pa (actual atmospheric pressure at location)
Result | 133040 | Pa
5.Calculation of oxygen content in per cent
Calculation Formula
Design parameters:
Ot- | 16.62% | Percentage of oxygen in the gas escaping from the aeration basin, dimensionless
EA- | 25% | Transfer coefficient of diffusion device, % oxygen utilisation (value selected with reference to technical parameters provided by SSI manufacturer)
Result | 0.16623
6.Calculation of average dissolved value
Calculation Formula
Design parameters:
Csm | 8.8189 | T℃、Average dissolved value of clear water from the depth of the water under which the actual aeration device is located to the surface of the pool, mg/1TC,
Csw | 8.38 | T℃、Saturated dissolved oxygen on the surface of clear water at actual calculated pressure, mg/1(CS(20)＝9.17mg/L，CS(25)＝8.38mg/L)
T- | 25 | ℃
Result | 8.8189 | mg/L
7.Calculation of oxygen demand correction factor
Calculation Formula
Design parameters:
KO- | 1.7146 | Oxygen demand correction factor
Co- | 2 | Remaining dissolved oxygen concentration of mixed liquid, mg/L
Cs | 9.17 | Saturated dissolved oxygen mass concentration in clear water under standard condition, mg/1
α- | 0.8 | Transfer efficiency resistance coefficient, the influence of the nature of wastewater on dissolved oxygen, correction factor K1a
Raw domestic sewagea value of about 0.4~0.5
Industrial wastewatera value varies greatly 0.8~0.85
The effect of salts in wastewater on dissolved oxygen, saturated oxygen resistance factor
β- | 0.9 | β value is generally between 0.9~0.97
Result | 1.7148
8.(Calculated on 24h basis) Aeration basin air supply volume Aeration basin air supply volume calculation
Calculation Formula
Design parameters:
Ro | 295.52 | kgO2/d
Gs | 12.31 | kgO2/h Aeration basin gas supply (24h)
Gs | 175.91 | m3/h
Gs | 2.93 | m3/min
Calculation Formula
Design parameters:
Gs max | 3.66 | m3/min
Gs max | 219.88 | m3/h
9.Air pressure required for aeration P (relative pressure)
Calculation Formula |  | P＝h1+h2+h3+h4+△h
Design parameters:
h1+h2 | 0.2 | m(Duct length and local resistance)
h3 | 4.3 | m(Aeration head submergence depth)
h4 | 0.3 | m(Aerator resistance)
△h | 0.5 | m(Have a high head of water)
P | 5.3 | m(Total air pressure0.53kg/m2)