## Sheet1
HANGZHOU JUNTAI PLASTIC PRODUCTS CO.LTD Head ofice : #3301, Times center, Linping ,Hangzhou, Zhejiang,China M:0086136 0051 3715 Email: info@juntaiplastic.com website: www.juntaiplastic.com
JUNTAI Aeration and Sand Sedimentation Tank Calculator
Blue block is the design datameter : be filled in Brown: calculate process data Red : last result for your process
1.JUNTAI Aeration Equipment----Design parameters:
Design flow rate | Q | 20000 | m3/d
Total coefficient of variation | Kz | 1.5
Design maximum flow rate | Qmax | 30000 | m3/d | 0.34722 | m3/s
2.JUNTAI Aeration Equipment----calculation result
Total effective volume of the pool | V=Qmax*t | 45.8333 | m3
Epidemic time at maximum design flow | t | 2.2 | min | 1~3
Water flow cross-section area | A=Qmax/v1 | 4.3403 | m2
Horizontal flow rate at maximum design flow | v1 | 0.08 | m/s | 0.06~0.12
Total pool width | B=A/h2 | 2.1701 | m
| Final take | 2.2 | m
Design effective water depth | h2 | 2 | m | 2~3m
Pool width per cell | b=B/n | 2.2 | m
Pool width to depth ratio | b/h2 | 1.1 |  | 1~1.5
Number of compartments | n | 1 | 格
Pool length | L=V/A | 10.56 | m
| Final take | 11 | m
Length to width ratio | L:b | 5 |  | Recommended aspect ratio 5：1
Total effective volume of pool | V | 45.8333 | m3
Cross-sectional area of water flow | A | 4.3403 | m2
Width of sand sedimentation tank opening | b1=2*h3*ctga+b2 | 0.31547 | m
Height of sinker | h3 | 0.1 | m
Angle between the sloping wall of the sinkhole and the horizontal plane | a | 60 | °
Width of the bottom of the sinkhole | b2 | 0.2 | m
Volume of each sedimentation tank | V1=(b1+b2)/2*h3*L | 0.27217 | m3
Total volume required for sand sedimentation tank | V=(Qmax*x*T*3600)/（Kz*106) | 1.2 | m3
Sand sedimentation volume | x | 30 | m3/m3 | Sewage
Sand injection time | T | 48 | h | ≤48h
Volume required for each sedimentation tank | V`=V/n | 1.2 | m3
Height of sloping part of tank bottom | h4=i*[(b-b1)/2] | 0.056536 | m
Over height | h1 | 0.3 | m
Slope of pool bottom | i | 0.06
Total pool height | H=h1+h2+h3+h4 | 2.4565 | m
Air volume required per hour | q=d*Qmax*3600 | 250 | m3/h | 4.1667 | m3/min
Air volume required for 1m3 sewage | d | 0.2 | m3/m3