## Sheet1
HANGZHOU JUNTAI PLASTIC PRODUCTS CO.LTD Head ofice : #3301, Times Center, Linping, Hangzhou, Zhejiang, China,311100 M:0086136 0051 3715 Email: info@juntaiplastic.com website: www.juntaiplastic.com
Juntai--Advection Air Flotation Tank Calculator
Blue block is the design datameter : be filled in Brown: calculate process data Red : last result for your process
Known:
Q= | 1800 | m3/d | Amount of wastewater to be treated
SS= | 700 | mg/L | Suspended solids concentration
Aa/S= | 0.02 |  | Gas-solid ratio
P= | 4.2 | atm | Dissolved air pressure
Ca= | 18.5 | mg/L | Saturated solubility of air in water
T1= | 3 | min | Dissolved air tank residence time
T2= | 5 | min | Contact time in air flotation tank
Ts= | 30 | min | Residence time in separation chamber
vs= | 0.09 | m/min | Rising flow rate in flotation tank
(1) Determination of The Amount of Dissolved Gas Water QR
QR= | Aa/S*Sa*Q/Ca(f*P-1)= |  | 896.1593 | m3/d
| Dissolved gas efficiency f= | 0.6
Take the return flow volume QR= |  | 900 | m3/d
(2) Air Flotation Tank Design
①Contact zone volume Vc
Vc= | (Q+QR)*T2/(24*60)= |  | 9.375 | m3
② Volume of separation area Vs
Vs= | (Q+QR)*Ts/(24*60)= |  | 56.25 | m3
③Air flotation tank effective water depth H
H= | vs*Ts= |  | 2.7 | m
④ Area of separation zone As and length L2
As= | Vs/H= |  | 20.8333 | m2
Take the pool width B = | 4 | m
Then the length of the separation zone L2= |  | As/B= | 5.2083 | m
⑤ contact area Ac and length L1
Ac= | Vc/H= |  | 3.4722 | m2
L1= | Ac/B= |  | 0.86806 | m
⑥Flotation cell inlet pipe: Dg=200,v=0.9947m/s
⑦Flotation Cell Outlet Pipe：Dg=150
⑧Collector pipe small hole area S
Take the small hole flow rate v1= |  | 1 | m/s
S= | (Q+QR)/24/3600v1= |  | 0.03125 | m2
Take the diameter of the small hole D1= |  | 0.015 | m
Then the number of holes n= | 4*S/3.14*D12= |  | 176.9285 | 个
The number of holes is taken as an integer, the mouth of the holes is downward, at an angle of 45° to the level, and is staggered in two rows.
⑨Float tank width L3:
取L3= | 0.8 | m
浮渣槽深度h′取1m，槽底坡度i=0.5，坡向排泥管，排泥管采用Dg=200.
(3)溶气罐设计
①溶气罐容积V1
V1= | QR*T1/(24*60)= |  | 1.875 | m3
溶气罐直径D=1.1m，溶气部分高度2m(进水管中心线）。采用椭圆形封头，曲面高为275mm，直边高为25mm，溶气罐耐压强度10×105Pa，溶气罐顶部设放气管Dg=15mm，排出剩余气体，并设置安全阀、压力表。
②进出水管管径：进出水管均采用100mm管径，管内流速为1.24m/s。